Work Paper WPSCREHC0001

Revision 1

Southern California Edison Company

Design & Engineering Services

Energy Star Room Air Conditioners

# At a Glance Summary

| Measure Name: | Energy Star Room Air Conditioners |
| --- | --- |
| Savings Impacts Common Units: | 12,906 Btu Weighted Mean Room Air Conditioner Unit |
| Customer Base Case Description: | 9.4 Weighted Mean EER (Current Code basis) |
| Code Base Case Description: | Same as Customer Base Case |
| Costs Common Units: | Same as Savings Impacts. |
| Measure Equipment Cost ($/unit): | $376.00 per room air conditioner |
| Measure Incremental Cost ($/unit): | $81.00 per room air conditioner |
| Measure Installed Cost ($/unit): | $0.00 |
| Measure Load Shape: | AC_Cooling-RC |
| Effective Useful Life (years): | 15 years |
| Program Type: | Replace On Burnout (ROB) and New |
| TOU AC Adjustment: | 100% |
| Net-to-Gross Ratios: | For Residential Contractor Program: 0.89 For all other residential programs: 0.80 |
| Building Type: | All Residential |
| Building Vintage: | All |
| Important Comments: | This work paper presumes the customer is either replacing a failed room air conditioner (RAC) or purchasing a RAC to be installed where there was no prior RAC. (This work paper also includes calculations and results for the Residential RAC Recycling to delineate efficiencies for the Residential RAC Recycling work paper and this work paper.) |

| Work Paper RunID WPSCREHC0001.1- | Climate Zone | Customer Annual Electric Savings (kWh/unit) | Customer Peak Electric Demand Reduction (kW/unit) | Above Code Annual Electric Savings (kWh/unit) | Above Code Peak Electric Demand Reduction (kW/unit) |
| --- | --- | --- | --- | --- | --- |
| 001 | 6 | 197.7 | 0.132 | 197.7 | 0.132 |
| 002 | 8 | 247.0 | 0.132 | 247.0 | 0.132 |
| 003 | 9 | 232.3 | 0.132 | 232.3 | 0.132 |
| 004 | 10 | 219.8 | 0.132 | 219.8 | 0.132 |
| 005 | 13 | 217.9 | 0.132 | 217.9 | 0.132 |
| 006 | 14 | 201.3 | 0.132 | 201.3 | 0.132 |
| 007 | 15 | 293.5 | 0.132 | 293.5 | 0.132 |
| 008 | 16 | 158.2 | 0.132 | 158.2 | 0.132 |

# Document Revision History

| Revision 0 | February 22, 2007 | Original short form work paper. |
| --- | --- | --- |
| Revision 1 | October 16, 2007 | Revision 0 (Rev 0) of this work paper was based on SCE engineering estimates of energy savings and demand reduction using Database for Energy Efficiency Resources (DEER) Annual Energy Consumption (kWh) per Multi-Family Apartment (RASS Weight Averaged) for a 14,000 Btu room air conditioner (RAC). Revision 1 (Rev 1) replaces the Rev 0 energy savings methodology with DEER database measure for Packaged Terminal Air Conditioners (PTAC) units for motel rooms as a basis. The PTAC measure is the only DEER measure using Energy Efficiency Ratios (EER) to measure performance for cooling of any kind: all other measures use the significantly different Seasonal EER. PTAC units are nearly identical to RACs in cooling performance but also provide heat. Establishing an equation for energy savings performance for PTAC EERs, Rev 1 uses a 12,906 Btu RAC and previous & current code and Energy Star room air conditioner EERs to establish energy savings. For demand reduction, Rev 1 retains the Rev 0 methodology. The DEER motel room PTAC measure’s 24 hour profile for power demand varies significantly from residential room air conditioner power demand profile. The table below lists values for Rev 0, Rev 1 and the change between the revisions. E3 Input; Rev 0; Rev 1; Change. Measure Cost; $106.00 per RAC; $81.00 per RAC; -$25.00 per RAC. Effective Useful Life; 15; 15; Unchanged. The table below lists the energy savings and demand reductions for Rev 0, Rev 1 and the change between the revisions. Rev 0 14,000 Btu RAC numbers were modified to 12,906 Btu RAC to match the RAC size of Rev 1. Energy Star RAC Summary: Rev 0 to Rev 1 Comparison. For One 12,906 Btu Room Air Conditioner. Climate Zone; Rev 0; Rev 1; Change; Climate Zone; Rev 0; Rev 1; Change. Energy Savings (kWh/square foot); Demand Reduction (kW/square foot). 6; 52; 198; 146; 6; 0.258; 0.132; -0.126. 8; 101; 247; 146; 8; 0.258; 0.132; -0.126. 9; 148; 232; 84; 9; 0.258; 0.132; -0.126. 10; 182; 220; 38; 10; 0.258; 0.132; -0.126. 13; 361; 218; -143; 13; 0.258; 0.132; -0.126. 14; 220; 201; -19; 14; 0.258; 0.132; -0.126. 15; 594; 293; -301; 15; 0.258; 0.132; -0.126. 16; 56; 158; 102; 16; 0.258; 0.132; -0.126. |

Note: The information provided in this Work Paper was developed using the best available technical resources at the time this document was prepared.

# Table of Contents

At a Glance Summary	i

Document Revision History	ii

Table of Contents	iii

List of Tables	iv

List of Figures	iv

Section 1. General Measure & Baseline Data	5

1.1 Measure Description & Background	5

1.2 DEER Differences Analysis	5

1.3 Codes & Standards Requirements Analysis	7

1.4 EM&V, Market Potential, and Other Studies	9

1.5 Base Cases for Savings Estimates: Existing & Above Code	10

1.6 Base Case & Measure Effective Useful Lives	11

1.7 Net-to-Gross Ratios for Different Program Strategies	11

Section 2. Calculation Methods	12

2.1 Energy Savings Estimation Methodologies	13

2.2. Demand Reduction Estimation Methodologies	23

Section 3. Load Shapes	23

3.1 Base Case Load Shapes	24

3.2 Measure Load Shapes	24

Section 4. Base Case & Measure Costs	25

4.1 Base Case Costs	25

4.2 Measure Costs	25

4.3 Incremental & Full Measure Costs	25

Appendices	26

Appendix A: RAC EER Design Variance Weighted Mean	26

References	31

# List of Tables

Table 1: DEER Table 6-1 (Partial): Nonresidential Space Characteristics	6

Table 2: DEER Table 6-2 (Partial): Nonresidential Prototype Descriptions	6

Table 3: DEER PTAC EER Values for Lodging - Motel	6

Table 4: 1605.1 (b) Table B-2 Standards for Room Air Conditioners and Room Air-Conditioning Heat Pumps	8

Table 5: 1605.1 (2) Table B-3 (Partial) Standards for Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps	9

Table 6: ENERGY STAR Qualified Room Air Conditioner (RAC) Eligibility	11

Table 7: Net-to-Gross Ratios	12

Table 8: Vintage Weighted Mean Slopes & Y Intercepts	16

Table 9: Example 2 - Climate Zone 6 Vintage Weighted Mean Linear Slope Calculations	16

Table 10: Example 2 - Climate Zone 6 Vintage Weighted Mean Y Intercept Calculations	17

Table 11: EER Weighted Mean by Unit Design for Cooling Capacity	18

Table 12: Example 3 - RAC Design Weighted Mean Values	19

Table 13: SCE Service Area: RAC Cooling Capacity Distribution	19

Table 14: Basis for determining the Population Weight Mean RAC for SCE Service Area	20

Table 15: Basis for determining the Weight Mean RAC EERs for SCE Service Area	21

Table 16: WM-RAC Annual Energy Savings (AES)	22

Table 17: Average Annual Energy Savings for a WM-RAC	23

Table 18: Weighted Mean RAC Demand Reduction	23

# List of Figures

Figure 1	12

Figure 2: TOU AC Cooling-RC Energy Share	24

Figure 3: TOU Peak kW Factors	25

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the E3 Calculator inputs for purchase of residential room air conditioners (RAC) that meet Energy Star requirements or Energy Star RACs (ES-RAC) instead of minimum efficiency Code RACs (C-RAC).  Thus, purchase of a C-RAC is the base case for this work paper and purchase of an ES-RAC is the measure case.  Installation costs are presumed to be identical.

In 1992 the U.S. Environmental Protection Agency (EPA)  introduced Energy Star as a voluntary labeling program designed to identify and promote energy-efficient products to reduce greenhouse gas emissions.  Through 1995, EPA expanded the label to additional office equipment products and residential heating and cooling equipment.  In 1996, EPA partnered with the U.S. Department of Energy (DoE) for particular product categories.  Energy Star announced labels for RACs in October 1996.  Energy Star RACs (ES-RAC) are defined as having a minimum of 10% energy efficiency improvement over minimum DoE requirements.

## 1.2 DEER Differences Analysis

This paper covers residential RAC applications.  However, there are no residential RAC application calculations available in the Database for Energy Efficiency Resources (DEER).  Residential DEER applications evaluate more efficient split systems and central air conditioning systems with higher Seasonal EER (SEER) requirements.

To determine energy savings, this work paper uses DEER Measure D03-099 which provides an analysis of Packaged Terminal Air Conditioners (PTAC  or Packaged Terminal Heat Pumps (PTHP) (collectively: PT units) installed in Motel Lodging Guest Rooms.  PT units use similar equipment to RACs for cooling, but also feature heating functions RACs do not have.  PT unit EERs are similar to RAC EER requirements.  This work paper uses PT unit vintage, code and 20% above code EERs and their related energy savings as points for Least Square Linear Regression (LSLR) Method) to establish a function to calculate equivalent RAC energy savings figures.

This work paper does not use DEER to determine demand reduction.  The twenty four hour Time-Of-Use (TOU) profile for DEER measure D03-099 is significantly different from residential RAC TOU.  Also, as the PT units include provisions for heating and RACs do not, this paper does not use the DEER cost data that would include capital costs for the PT unit heating elements.

In DEER Section 6 for Motel Lodging Guest Rooms Table 1 and  list the following information:

Table 1: DEER Table 6-1 (Partial): Nonresidential Space Characteristics

| Activity Area Type | Occupant Density (ft2/person) | Sensible Occupant Load (Btuh/person) | Latent Occupant Load (Btuh/person) | Ventilation Rate (cfm/person) |
| --- | --- | --- | --- | --- |
| Motel Guest Room | 300.0 | 245 | 155 | 30.00 |

Table 2: DEER Table 6-2 (Partial): Nonresidential Prototype Descriptions

| Prototype | Source | Activity Area Type | Area | % Area | Simulation Model Notes |
| --- | --- | --- | --- | --- | --- |
| 10. Lodging - Motel | DEER | Corridor | 3,333 | 11.1 | Thermal Zoning: One zone per activity area. Model Configuration: Matches 1994 DEER configuration. Guestrooms are divided among: 12 hour occupied (12,794 ft2/ 42.6%), 24-hour occupied (6,397 ft2/ 21.3%) and unoccupied rooms (6,397 ft2/ 21.3%). HVAC Systems: The oldest vintage uses PTAC systems with electric resistance heating. All other vintages use PTHP systems. |
|  |  | Motel Guest Room (incl. toilets) | 25,587 | 85.3 |  |
|  |  | Laundry | 480 | 1.6 |  |
|  |  | Office (General) | 600 | 2.0 |  |
|  |  | Total | 30,000 |  |  |

Table 1 lists DEER loads and ventilation rates for Motel Lodging Guest Rooms.  The Lodging – Motel section from DEER Table 6-2 identifies PTAC and PTHP ( above) as being used in the simulation of Motel Lodging Guest Rooms.  The Motel Lodging Guest Room applications appear to be best available DEER simulation for residential RAC applications which are most likely to be for cooling one room with some interior and some exterior walls and ceilings.  DEER Measure D03-099 Run IDs differ from the  description stating all vintages in the Measure use PTACs.

Motels on average are cooled at 1 ton of cooling (12,000 Btu) per 300 square feet (ft2).  Based on the DEER occupant density of 300 ft2 this paper sets PT units at 12,000 Btu cooling 300 ft2.  The DEER Lodging – Motel total floor area is 30,000 ft2 so dividing total floor area by 300 ft2 results in 100 total PT units installed in the DEER Lodging – Motel.

DEER uses the PTAC EER values listed in Table 3 below:

Table 3: DEER PTAC EER Values for Lodging - Motel

| DEER: PTAC (7-15 kBtu/unit or 0.583 to 1.25 cooling tons/unit) |  |  |  |
| --- | --- | --- | --- |
| Buildings Vintages | Measure Case Description (EER) | Base Case Description (EER) | Code Base Description (T24 minimum EER) |
| Built before 1978 | 10.27 | 6.80 | 8.56 |
| Built between 1978 and 1992 | 10.27 | 7.80 | 8.56 |
| Built between 1993 and 2001 | 10.27 | 8.50 | 8.56 |
| Built between 2002 and 2005 | 10.27 | 8.50 | 8.56 |
| Built 2006 and later (measures as retrofit for nonresidential) | 12.19 | 10.16 | 10.16 |

## 1.3 Codes & Standards Requirements Analysis

U.S. DoE Office of Energy Efficiency and Renewable Energy Energy’s “Conservation Program for Consumer Products: Final Rule Regarding Energy Conservation Standards for Room Air Conditioners: 10 CFR Part 430” is summarized in the State of California Code Of Regulations, Title 20: Division 2, Chapter 4, Article 4, Appliance Efficiency Regulations (Title 20).

Definitions

Title 20 establishes the following selected definitions in Section 1602(c) Air Conditioners:

“Air conditioner” means an appliance that supplies cooled air to a space for the purpose of cooling objects within the space.

“Air-source heat pump” means an appliance that consists of one or more factory-made assemblies, that includes an indoor conditioning coil, a compressor, and a refrigerant-to-air heat exchanger, and that provides heating and cooling functions.

“Btu” means British thermal unit. .

“Casement-only room air conditioner” means a room air conditioner with an encased assembly designed for mounting in a casement window with a width of 14.8 inches or less and a height of 11.2 inches or less.

“Casement-slider room air conditioner” means a room air conditioner with an encased assembly designed for mounting in a sliding or casement window with a width of 15.5 inches or less.

“Casement window” means a window that opens on hinges at the side.

“Coefficient of Performance (COP)” of a heat pump means the ratio of the rate of useful heat output delivered by the complete heat pump unit (exclusive of supplementary heating) to the corresponding rate of energy input, in consistent units and as determined using the applicable test method in Section 1604(b) or 1604(c).

“Cooling capacity” means a measure of the ability of an air conditioner to remove heat from an enclosed space, as determined using the applicable test method in Section 1604(b) or 1604(c).

“Energy efficiency ratio (EER)” means the cooling capacity of an air conditioner in Btu per hour divided by the total electrical input in watts, as determined using the applicable test method in Section 1604(b) or 1604(c).

“Heat pump” means an appliance, other than a packaged terminal heat pump, that consists of one or more assemblies; that uses an indoor conditioning coil, a compressor, and a refrigerant-to-outdoor air heat exchanger to provide air heating; and that may also provide air cooling, dehumidifying, humidifying, circulating, or air cleaning.

“Packaged Terminal Air Conditioner” (PTAC) means a wall sleeve and a separate un-encased combination of heating and cooling assemblies that:

(1) is intended for mounting through the wall and

(2) includes a prime source of refrigeration, separable outdoor louvers, forced ventilation, and heating availability by hot water, steam, or electric resistance heat.

“Packaged Terminal Heat Pump” (PTHP) means a packaged terminal air conditioner that uses reverse cycle refrigeration as its prime heat source and that has a supplementary heat source of hot water, steam, or electric resistance heat.

“Room Air Conditioner” (RAC) means a factory-encased air conditioner that is designed:

(1) as a unit for mounting in a window, through a wall, or as a console, and

(2) for delivery without ducts of conditioned air to an enclosed space.

“Room air-conditioning heat pump” means a room air conditioner that is capable of heating by refrigeration.

“Seasonal energy efficiency ratio (SEER)” means the total cooling output of an air-cooled central air conditioner during its normal annual usage period for cooling, divided by the total electrical energy input in watt-hours during the same period, as determined using the applicable test method in Section 1604(c).

While PTAC units can also provide heat thru either in-unit or externally supplied sources, this paper does not evaluate efficiency of PTAC heating.

RAC Requirements

As stated in Section 1605.1 (b), code took effect as of Jan 1, 1990, several years before the advent of Energy Star.  Code was revised as of Oct 2000 to the higher current standard.  This enactment date was after the calendar year 2000 air conditioning season so energy savings and demand reduction due to this code change would not take effect until calendar year 2001.

Section 1605.1 (b) Room Air Conditioners, Room Air-Conditioning Heat Pumps, Packaged Terminal Air Conditioners, and Packaged Terminal Heat Pumps.

(1) Room Air Conditioners and Room Air-Conditioning Heat Pumps. The EER of room air conditioners and room air-conditioning heat pumps that are manufactured on or after the effective dates shown shall be not less than the applicable values shown in Table B-2. The EER of room air conditioners and room air-conditioning heat pumps that are labeled for use at more than one voltage shall be not less than the applicable values shown in Table B-2 at each of the labeled voltages.

Table 4: 1605.1 (b) Table B-2 Standards for Room Air Conditioners and Room Air-Conditioning Heat Pumps

| Appliance | Louvered Sides | Cooling Capacity (Btu/hr) | Minimum EER or COP |  |
| --- | --- | --- | --- | --- |
|  |  |  | Effective January 1, 1990 | Effective October 1, 2000 |
| Room Air Conditioner | Yes | < 6,000 | 8.0 | 9.7 |
| Room Air Conditioner | Yes | ≥ 6,000 - 7,999 | 8.5 | 9.7 |
| Room Air Conditioner | Yes | ≥ 8,000 - 13,999 | 9.0 | 9.8 |
| Room Air Conditioner | Yes | ≥ 14,000 - 19,999 | 8.8 | 9.7 |
| Room Air Conditioner | Yes | ≥ 20,000 | 8.2 | 8.5 |
| Room Air Conditioner | No | < 6,000 | 8.0 | 9.0 |
| Room Air Conditioner | No | ≥ 6,000 - 7,999 | 8.5 | 9.0 |
| Room Air Conditioner | No | ≥ 8,000 - 19,999 | 8.5 | 8.5 |
| Room Air Conditioner | No | ≥ 20,000 | 8.2 | 8.5 |
| Room Air Conditioning Heat Pump | Yes | < 20,000 | 8.5 | 9.0 |
| Room Air Conditioning Heat Pump | Yes | ≥ 20,000 | 8.5 | 8.5 |
| Room Air Conditioning Heat Pump | No | < 14,000 | 8.0 | 8.5 |
| Room Air Conditioning Heat Pump | No | ≥ 14,000 | 8.0 | 8.0 |
| Casement-Only Room Air Conditioner | Either | Any | * | 8.7 |
| Casement-Slider Room Air Conditioner | Either | Any | * | 9.5 |
| *Casement-only room air conditioners and casement-slider room air conditioners are not separate product classes under standards effective January 1, 1990. Such appliances, if manufactured before October 1, 2000, are subject to the applicable standards in Table B-2 for the other room air conditioners and room air-conditioning heat pumps based on capacity and the presence or absence of louvered sides. |  |  |  |  |

The Minimum EER or COP Effective October 1, 2000 column lists the current code requirements for C-RAC units.  In Section 2.1, this work paper combines these various design and capacity EERs into a weighted mean EER for energy savings evaluation.

PTAC Requirements

Section 1605.1.2 defines Code requirements for the PT Units.  For this work paper, these figures are only applicable to the determination of the LSLR Method for EER to Energy Savings Equations used to then determine energy savings for RACs in Section 2.1.

Section 1605.1 (2) Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps. The EER and COP, as applicable, of packaged terminal air conditioners and packaged terminal heat pumps shall be not less than the applicable values shown in Table B-3.

Table 5: 1605.1 (2) Table B-3 (Partial) Standards for Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps

| Appliance | Mode | Cooling Capacity (Btu/hr) | Minimum EER or COP |
| --- | --- | --- | --- |
| Packaged terminal air conditioners and packaged terminal heat pumps | Cooling | =< 7,000 | 8.88 EER |
|  |  | > 7,000 and < 15,000 | 10.0 - (0.00016 x Cap.) EER |
|  |  | >=15,000 | 7.6 EER |

## 1.4 EM&V, Market Potential, and Other Studies

The Residential Appliance Saturation Survey (RASS) 2003 indicates an annual Unit Energy Consumption (UEC) of 240 kWh for RACs in the Southern California Edison (SCE) service area and statewide:

“Room air conditioning has a UEC of 214 kWh and evaporative systems 684 kWh.  These values are somewhat lower than previous studies and forecasting values used at the Energy Commission.  One possible reason for the lower than average use is attributed to the Statewide 20/20 Program.  Billing data for the Conditional Demand Analysis is from the second half of 2001, all of 2002, as well as 2003 and 2004 to include years when the 20/20 program was not available. UEC results have all been annualized and calibrated to 2002 service territory total usage. It is likely that the UECs reflect the 20/20 program impact and thus these air conditioning values should be considered conservative estimates.”

The RASS states:

“A similar (to central air conditioning) albeit more parsimonious specification will be used for room air conditioning (RACUSEht), except that a term will be used to reflect the number of room air conditioning units (RACCNTh). This stems from the assumption that total usage depends on the number of room air conditioners.”

The RASS states RAC:

“Unit Energy Consumptions are also fairly low relative to prior estimates, varying from 105 kWh for multi-family units in buildings with 5+ units to 227 kWh for single family homes and mobile homes.”

The RASS does not state:

1)	Size, design or capacity of RACs analyzed,

2)	EERs of RACs or

3)	Square footage cooled.

Without this information it is difficult to compare the RASS information to other sources in this work paper.  There appears to be some questioning even in the RASS verbiage as to the accuracy of the UEC RAC figures.

The RASS estimates about 20 percent of SCE homes have room air conditioners.  The SCE Residential Room Air-Conditioner Recycling Scoping Study (Scoping Study) estimates 50% of those homes have units ten years old or more, similar to the RASS estimate of 47% of homes that have units more than nine years old.  The average age of room air conditioners in RASS data is calculated to be 7.71 years.

For a Weighted Mean RAC (WM-RAC) that provides 12,906 Btu of cooling and averaging estimated energy savings for all climate zones, replacing a Jan 1990 code RAC with an Energy Star RAC produces a total annual 397.7 kWh/WM-RAC unit savings (From Table 17).  This number compares with the 372.2 kWh/ room air conditioner unit annual savings reported for multifamily housing in the Low-Income Energy Efficiency (LIEE) program.

## 1.5 Base Cases for Savings Estimates: Existing & Above Code

The base case is a C-RAC that meets the Federal Standard EER requirements.  For this work paper, Customer Savings and Above Code Savings  estimates are the same and are based on the Energy Star EERs as defined in Table 6: Energy Star Qualified RAC Eligibility.  Customer Savings from early retirement of existing RAC (vintage code to current code) are only counted in the separate Room Air Conditioner Recycling Work Paper.

Federal Standard and Energy Star Energy Efficiency Ratio (EER) requirements are detailed in Table 6.  As Title 20 has adopted these Federal Standard EERs, this paper refers to the Federal Standards as Title 20 code.

Table 6: ENERGY STAR Qualified Room Air Conditioner (RAC) Eligibility

| Capacity (Btu/Hr) | Federal Standard EER, with louvered sides | ENERGY STAR EER, with louvered sides | Federal Standard EER, without louvered sides | ENERGY STAR EER, without louvered sides |
| --- | --- | --- | --- | --- |
| < 6,000 | ≥ 9.7 | ≥ 10.7 | ≥ 9.0 | ≥ 9.9 |
| 6,000 to 7,999 |  |  |  |  |
| 8,000 to 13,999 | ≥ 9.8 | ≥ 10.8 | ≥ 8.5 | ≥ 9.4 |
| 14,000 to 19,999 | ≥ 9.7 | ≥ 10.7 |  |  |
| ≥ 20,000 | ≥ 8.5 | ≥ 9.4 |  |  |
| Casement | Federal Standard EER |  | ENERGY STAR EER |  |
| Casement-only | ≥ 8.7 |  | ≥ 9.6 |  |
| Casement-slider | ≥ 9.5 |  | ≥ 10.5 |  |
| REVERSE CYCLE |  |  |  |  |
| Capacity (Btu/Hr) | Federal Standard EER, with louvered sides | ENERGY STAR EER, with louvered sides | Federal Standard EER, without louvered sides | ENERGY STAR EER, without louvered sides |
| < 14,000 | n/a | n/a | ≥ 8.5 | ≥ 9.4 |
| ≥ 14,000 |  |  | ≥ 8.0 | ≥ 8.8 |
| < 20,000 | ≥ 9.0 | ≥ 9.9 | n/a | n/a |
| ≥ 20,000 | ≥ 8.5 | ≥ 9.4 | n/a | n/a |

## 1.6 Base Case & Measure Effective Useful Lives

- A table in the ASHRAE HVAC Equipment Handbook indicates the Effective Useful Life (EUL) for window unit RACs is ten years and fifteen years for all other air conditioning units and heat pumps.  However, a footnote to that same table also indicates this data from Akalin (1978) “may be outdated and not statistically relevant.  Use this data with caution until enough updated data are accumulated in Abramson et. al.”.

- The Association of Home Appliance Manufacturers (AHAM) web site includes a 1996 survey by National Family Opinion, Inc. (NFO) stating the EUL for RACs is 12 years.  The NFO’s basis for EUL is: “age of an appliance when it is replaced because it cannot be repaired or costs too much to repair.  (This does not infer the appliance will be without repair during its lifetime.)”.

- The Table of Discarded Window/Wall (RAC) AGE (DWWAGE) by Window/Wall (RAC) ADDed (WWADD) from the RASS 2003 data of homes that replaced their old wall/window RAC with a new unit, 20.59% of replaced units were up to ten years old, 38.71% were 11 to 20 years old and the remaining 40.70% units were more than 20 years old.  Based on the RASS 2003 study, this paper uses a new RAC EUL for the SCE region of the half life of these units: 15 years.

## 1.7 Net-to-Gross Ratios for Different Program Strategies

This work paper covers customer driven appliance Replace on Burnout  (ROB) and New Construction of RACs in residential installation.  Per the CPUC Energy Efficiency Policy Manual and on the DEER web site the Net-to-Gross (NTG) ratio is 0.80 for all programs except the Residential Contractor program.  For Residential Contractor replaced units, the NTG ratio is 0.89.

Table 7: Net-to-Gross Ratios

| Residential Construction | Program Approach | NTG |
| --- | --- | --- |
| Multifamily unit | Residential Contractor Program | 0.89 |
| All unit | All other residential programs | 0.80 |

# Section 2. Calculation Methods

No study was available to quantify either where in what type of residence one or more RACs may be located or how many people may be in what size of how much conditioned space.

DEER Measure ID D03-099 Run IDs (DEER Calcs) is the only DEER measure evaluating similar equipment cooling performance in EER.  This measure evaluates PT units installed in the DEER two story building model Lodging-Motel.  The construction elements used in the Lodging-Motel model are similar to residential construction elements.  The measure also randomly loads PTAC units with mixed interior and exterior floors, walls and ceilings and mixes operating hours between none, 12 hour and 24 hour operation.

The randomness of PTAC unit installation and operation provides something of a reasonable basis for estimating RAC energy savings.  However, the DEER PTAC 24-hour usage distribution (percentage of the motel that is actively being cooled: Figure 1) does not match a typical residential air conditioning end use profile.  Therefore, RAC power demand was estimated at full power demand during a three day heat wave in the SCE service area.

DEER Lodging-Motel Model: PT Unit 24 Hour Usage Distribution

0%

10%

20%

30%

40%

50%

60%

70%

80%

1

3

5

7

9

11

13

15

17

19

21

23

Hour of Day

Cooled

Square

Footage

Percentile

Figure 1 Hotel Room PTAC Usage

## 2.1 Energy Savings Estimation Methodologies

This work paper takes DEER data for PT units and uses the LSLR Method to establish an EER to energy savings equation for each motel building vintage in each SCE climate zone.  By weighing the equation slope and Y intercept by motel building population data for each vintage in a climate zone a vintage weighted mean EER to energy savings equation is established for each climate zone.

To determine a single RAC cooling capacity with C-RAC and ES RAC EERs, this work paper establishes the following.  For each cooling capacity range in British thermal units (Btu) all unique RAC units listed in the Energy Star web site are counted for each design type with that number divided by the total RACs of the same capacity.  Using the percentage of units SCE rebated (SCE Rebate Scale) for each Btu range and translating the SCE ranges to match the Title 20 code Btu ranges, this work paper establishes an cooling capacity weighted mean RAC for evaluation in each climate zone.  Using the same SCE Rebate Scale this paper further weights the design weighted mean EERs to establish EERs for the WM-RAC.  Using the energy savings equation, this paper estimates energy savings for both codes and Energy Star RAC in each climate zone.

LSLR Method for Equations

The DEER Calcs provide estimated energy savings for replacing vintage PT units with PT units that meet T24 minimum EER code requirements and 20% higher efficiency EER PT units.

The first point is set at the X-axis intercept (no energy savings) DEER base case EER found in the DEER Calcs: Base Case Description.  This point represents the existing PT units in each DEER model which meet each building vintage’s Nonresidential Compliance Manual For California's 2005 Energy Efficiency Standards (Title 24) code requirements, if any.

- DEER building vintage Title 24 construction code EER: X1;
YE1 - energy savings equal zero (Xi – X-axis Intercept),

The second point represents the fact the Title 24 code requires the building vintage PT units be upgraded on replacement to at least the current Title 20 EER figure.  This upgrade produces the code energy savings (ECImpact).

- DEER Basis 2000 Title 20 code EER: X2; YE2 - ECImpact

The third point is the DEER measure energy savings (EImpact).

- DEER measure EER: X3; YE3 - EImpact

Using these figures for each vintage and climate zone and LSLR Method, an equation expressing energy savings for various EERs is established.  The following variables are used in the LSLR Method:

Xa is any EER value,

YEa is the corresponding energy efficiency savings to the Xa figure,

n is the total number of data points (n = 3 for these calculations), and

Σ is the Greek Letter sigma that stands for summation.  Equation (1) is an example:

Σ(Xa) = X1 + X2 + X3	(1)

Equation (2) is used to determine a linear slope (SE):

SE = (n*Σ(Xa*YEa) - Σ(Xa)*Σ(YEa))/(n* Σ(Xa2)- (ΣXa) 2	(2)

Once SE is determined, the Y intercept (YEi) where EER equals zero can be determined by Equation (3):

YEi = (Σ(YEa) - S * Σ(Xa))/n	(3)

By determining SE and YEi, this paper establishes an EER to energy savings equation for each building vintage within a climate zone (Equation (4)):

YEa = YEi + SE * Xa	(4)

Data and calculations for all forty of the SE and YEi values are detailed in DEER Measure D03-099 Lodging-Motels.xls: Sheet: LSLR Method & Vintage Weighing.

Example 1 - LSLR Method for Equations

Determine the Slope (SE) and Y intercept (YEi) for the EER to energy savings equation for a 12,000 Btu PTAC unit installed in a motel built before 1978 in the City of Long Beach.

DEER Measure ID D03-099 Run ID CMtl0675PTAC2 provides estimated energy savings for replacing a vintage PT unit with a PT unit that meets T24 current minimum EER code requirements and 20% higher efficiency EER PT unit installed in a motel built before 1978 in the City of Long Beach.  The DEER common units are Cooling Tons (CTon) or 12,000 Btu.  DEER energy savings are in kilowatt-hour (kWh) per CTon.

The first point is set at the X-axis intercept (no energy savings) DEER base case EER found in the DEER Calcs: Base Case Description.  This point represents the existing PT units in each DEER model which meet each building vintage’s Title 24 code requirements, if any.

- DEER building vintage Title 24 construction code EER: X1 = 6.80;
YE1 is where energy savings equal zero: (Xi – X-axis Intercept): YE1 = 0 kWh/CTon,

The second point represents the fact the Title 24 code requires the building vintage PT units be upgraded on replacement to at least the current Title 20 EER figure.  This upgrade produces the code energy savings ECImpact.

- DEER Basis 2000 Title 20 code EER: X2; = 8.56; ECImpact YE2 = 277.691 kWh/CTon

The third point is the DEER measure energy savings (EImpact).

- DEER measure EER: X3; = 10.27; EImpact YE3 = 709.349 kWh/CTon

Using these figures and LSLR Method, an equation expressing energy savings for various EERs is established.  The following variables are used in the LSLR Method:

Xa is any EER value,

Ya is the corresponding energy efficiency savings to the Xa figure,

n is the total number of data points (n = 3 for these calculations), and

Σ is the Greek Letter sigma that stands for summation.

Variables for Equation (2) are:

Σ(Xa) 	= X1 + X2 + X3 = 6.80 + 8.56 +10.27 = 25.63

Σ(Xa2) 	= (X1 * X1) + (X2 * X2) + (X3 * X3) 
= (6.80 * 6.80) + (8.56 * 8.56) + (10.27 * 10.27) = 224.987

Σ(YEa) 	= YE1 + YE2 + YE3 = 0 + 277.691 + 709.349 = 987.040

Σ(Xa*YEa) 	= X1 * YE1 + X2 * YE2 + X3 * YE3 
= 6.8 * 0 + 8.56 * 277.691 + 10.27 * 709.349 = 9,662.049

Equation (2) is used to determine the linear slope (SE):

SE 	= (n*Σ(Xa*Ya) - Σ(Xa)*Σ(Ya))/(n* Σ(Xa2)- (ΣXa) 2
= (3 * 9,662.049 - 25.63 * 987.040) / (3 * 224.987 – (25.63 * 25.63)
= 204.196

Once S is determined, the Y intercept (YEi) where EER equals zero can be determined by Equation (3):

YEi 	= (Σ(YEa) - SE * Σ(Xa))/n = (987.040 - 204.196 * 25.63) / 3
= -1415.502

By determining SE and YEi, the EER to energy savings equation (Equation (4)) is:

YEa = YEi + SE * Xa = -1415.502 + 204.196 * Xa

Data and calculations for the SE and YEi values and a graph of the resulting equation are detailed in DEER Measure D03-099 Lodging-Motels.xls: Sheet: LSLR Method Example+Graph.

Vintage Weighted Mean Equations

Using the YEia for each building vintage (YEi1 thru YEi5) allows the vintage weighted mean (YEvwm) for all vintages in a climate zone to be determined.  The Commercial End Use Saturation surveys (CEUS) provides a basis for a total number of buildings (NLOCS) per each building vintage within the same climate zone.  This work paper uses DEERCD building type MTL (Motel) and establishes a variable NLOCSa which is the NLOCS value for a particular vintage within the same climate zone.  Thus, NLOCS1 thru NLOCS5 are the total number of buildings for each building vintage oldest to newest.  Equation (5) calculates the weighted mean YEi (YEvwm) for all vintages of the building per climate zone:

YEvwm = (Σ(NLOCSa* YEia)) / Σ(NLOCSa)	(5)

In a similar way, using the slope SEa for each building vintage of a climate zone (SE1 thru SE5) the vintage weighted mean slope (SEvwm) can be determined (in equation (5): YE becomes SE).

By determining YEvwm and SEvwm, this paper establishes an equation of EER to energy savings for each climate zone (Equation (6)):

YEa = YEvwm + SEvwm * Xa	(6)

Data and calculations for all YEvwm and SEvwm values are detailed in DEER Measure D03-099 Lodging-Motels.xls: Sheet: LSLR Method & Vintage Weighing.  The resulting values are listed in Table 8.

Table 8: Vintage Weighted Mean Slopes & Y Intercepts

| Vintage Weighted Mean Slopes & Y Intercepts |  |  |  |
| --- | --- | --- | --- |
| DEER Values |  | Energy Savings: |  |
| Climate Zone City | CA T24 CZ: | Weighted Slope | Weighted Y Intercept |
|  |  | SEa | YEia |
| Long Beach | 6 | 183.835 | -1,297.400 |
| El Toro | 8 | 229.651 | -1,624.025 |
| Burbank | 9 | 216.026 | -1,537.142 |
| Riverside | 10 | 204.380 | -1,458.538 |
| Fresno | 13 | 202.615 | -1,423.334 |
| China Lake | 14 | 187.204 | -1,323.838 |
| El Centro | 15 | 272.872 | -1,912.036 |
| Mt. Shasta | 16 | 147.093 | -1,033.533 |

Example 2 - Vintage Weighted Mean Equation

Given the slopes (SEa) and Y intercepts (YEia) for each DEER vintage of motel built in Long Beach, find the vintage weighted mean linear slope, Y intercept and the EER to energy savings equation on a cooling ton basis.

For the slope calculation, the required data from the “LSLR Method & Vintage Weighing” sheet of “DEER Measure D03-099 Lodging-Motels.xls” are the CEUS Weight Factors NLOCSa and the LSLR Method Slopes SEa for each building vintage.  Multiplying the SEa by the respective NLOCSa produces the Vintage Weighting Factor (SEa * NLOCSa) for each vintage.  Values for these variables are shown in Table 9.

Table 9: Example 2 - Climate Zone 6 Vintage Weighted Mean Linear Slope Calculations

| For Motels in Long Beach Climate Zone 6: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Buildings Vintages | Vintage Order | CEUS Weight Factors | LSLR Method Slopes | Vintage Weighting Factors |
|  |  | NLOCSa | SEa | (SEa *NLOCSa) |
| Built before 1978 | 1 | 254 | 204.196 | 51,866 |
| Built between 1978 and 1992 | 2 | 107 | 164.463 | 17,598 |
| Built between 1993 and 2001 | 3 | 14 | 77.640 | 1,087 |
| Built between 2002 and 2005 | 4 | 10 | 76.968 | 770 |
| Built 2006 and later (measures as retrofit for nonresidential) | 5 | 4 | 47.907 | 192 |
| Totals (Σ): |  | 389 |  | 71,512 |

Equation (5) modified to calculate the weighted mean SE (SEvwm) for all vintages of the building type per climate zone is:

SEvwm = (Σ(NLOCSa * SEa)) / Σ(NLOCSa) = 71,512 / 389 = 183.835

For the Y intercept calculation, the required data from the “LSLR Method & Vintage Weighing” sheet of “DEER Measure D03-099 Lodging-Motels.xls” are the CEUS Weight Factors NLOCSa and the LSLR Method Y intercepts YEia for each building vintage.  Multiplying the YEia by the respective NLOCSa produces the Vintage Weighting Factor (YEia * NLOCSa) for each vintage.  Values for these variables are shown in Table 10.

Table 10: Example 2 - Climate Zone 6 Vintage Weighted Mean Y Intercept Calculations

| For Motels in Long Beach Climate Zone 6: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Buildings Vintages | Vintage Order | CEUS Weight Factors | LSLR Method Y intercepts | Vintage Weighting Factors |
|  |  | NLOCSa | YEia | (YEia *NLOCSa) |
| Built before 1978 | 1 | 254 | -1,415.502 | -359,537 |
| Built between 1978 and 1992 | 2 | 107 | -1,220.122 | -130,553 |
| Built between 1993 and 2001 | 3 | 14 | -545.310 | -7,634 |
| Built between 2002 and 2005 | 4 | 10 | -540.586 | -5,406 |
| Built 2006 and later (measures as retrofit for nonresidential) | 5 | 4 | -389.487 | -1,558 |
| Totals (Σ): |  | 389 |  | -504,689 |

Equation (5) calculates the weighted mean YEi (YEvwm) for all vintages of the building type per climate zone:

YEvwm = (Σ(NLOCSa* YEia)) / Σ(NLOCSa) = -504,689 / 389 = -1,297.400

For Motels in Long Beach Climate Zone 6, the EER to energy savings Equation (5) is:

YEa = YEvwm + SEvwm * Xa = -1,297.400 + 183.835 * Xa

MS Excel versions of Table 9 and Table 10 are shown in the “Vintage Weighted Mean Example” sheet of “DEER Measure D03-099 Lodging-Motels.xls”.

RAC EER Design Variance Weighted Mean Values

The Energy Star Web site provides a list of available Energy Star RACs from 5,000 to 28,000 Btu/hr cooling capacity.  This list includes various design details like which RACs have reverse cycles (Heat Pumps), side louvers and or casement-only or slider style units.  Title 20 Table B-2 lists code EERs based on those design details for various cooling capacity ranges.  Counting the available unique units with each of these design characteristics and cooling capacities provides a design weighing factor to determine a design weighted mean RAC EER for the Title 20 Table B-2 cooling capacity ranges.  This work paper adds together the counts of unique units with similar RAC EER & cooling capacities and then finds a design variance weighted mean EER for each Title 20 Table B-2 cooling capacity range.  The resulting EERs are shown in Table 11.

Table 11: EER Weighted Mean by Unit Design for Cooling Capacity

| EER Weighted Mean by Unit Design for Cooling Capacity |  |  |
| --- | --- | --- |
| Cooling Capacity (Btu/hr) | Effective January 1, 1990 | Effective October 1, 2000 |
| < 6,000 | 8.00 | 9.69 |
| ≥ 6,000 - 7,999 | 8.50 | 9.64 |
| ≥ 8,000 - 13,999 | 8.77 | 9.27 |
| ≥ 14,000 - 19,999 | 8.78 | 9.65 |
| ≥ 20,000 | 8.22 | 8.50 |

Complete tables of Energy Star Product Listings and calculations for Unique Unit Design Weighted Mean EERs are listed in Appendix A: RAC EER Design Variance Weighted Mean and in the “EER Weighting by Unique Units” sheet of MS Excel Workbook “Energy Star RACs-20070802.xls”.

Example 3 - RAC EER Design Variance Weighted Mean Values

Count the RACs with capacities equal to or greater than 8,000 and less than 13,999 Btu by unique design features listed in the Energy Star web site to determine the number of Unique Unit (UUs) RACs.  Find the EER Weighted Mean Factor for each type of these UU designs and the weighted mean EER for all of these UU RAC units.

Example 3 column & row references can be found in Table 12 below.  The Energy Star web site lists four unique designs for RACs with capacities equal to or greater than 8,000 and less than 13,999 Btu: standard RACs with & without louvered sides and heat pumps with & without louvered sides (columns (A) & (B) in T-X).  Also listed are the Jan 1990 and Oct 2000 minimum EERs for each of these designs (columns (C) & (D)).

Counting the number of unique RACs listed in the Energy Star Product Listing results in the numbers in column (E).  Column (F) shows the addition of ten 8,000 Btu casement units from Row 27 to Row 11 which have identical EERs with the results of the addition in column (G) and subtotal of all the 8,000 and less than 13,999 Btu manufacturer RACs.

For Row 11:	(G) = (E) + (F) = 310 + 10 = 320

Column (H) is the column (G) number divided by the column (G) subtotal resulting in the percentile of each unique design relative to the total number of unique designs:

Row 15 Column (G) Subtotal: Σ(G) = 320 + 193 + 20 + 19 = 552

For Row 11:	(H) = (G) / Σ(G) = 320 / 552 = 0.58 or 58.0%

Columns (I) & (J) are the Minimum EERs (columns (C) & (D)) multiplied by the percentile.

For Row 11:	(I) = (C) * (H) = 9.0 * 0.58 = 5.22

(J) = (D) * (H) = 9.8 * 0.58 = 5.68

Summing column (I) results in the design weighted EER of 8.77 for the Jan 1990 Code.

Row 15 Column (I) Subtotal: Σ(I) = 5.22 + 2.97 + 0.31 + 0.28 = 8.77

Summing column (J) results in the design weighted EER of 9.27 for the Oct 2000 Code.

Row 15 Column (J) Subtotal: Σ(J) = 5.68 + 2.97 + 0.33 + 0.29 = 9.27

Table 12: Example 3 - RAC Design Weighted Mean Values

|  | Cells in Blue Arial font are from Title 20 Table B-2 |  |  |  | Energy Star Product Search Unique Units (UU) |  |  |  | EER Weighted Mean Factors by Unit Design for Capacity |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Row: | Appliance | Louvered Sides | Minimum EER |  |  |  |  |  |  |  |
|  |  |  | Effective Jan 1990 | Effective Oct 2000 | No. of UUs | Adjust-ments to equiv. EERs | Adjust-ed No. of UUs | % of UUs per Cap | Effective Jan 1990 | Effective Oct 2000 |
|  | Column (A) | (B) | (C) | (D) | (E) | (F) | (G) = (E)+(F) | (H) = (G) / Subtotal | (I) = (C)*(H) | (J) = (D)*(H) |
|  | For Capacities ≥ 8,000 - 13,999 Btu/hr |  |  |  |  |  |  |  |  |  |
| 11 | RAC | Yes | 9.0 | 9.8 | 310 | 10 from Row 27 | 320 | 58.0% | 5.22 | 5.68 |
| 12 | RAC | No | 8.5 | 8.5 | 193 | None | 193 | 35.0% | 2.97 | 2.97 |
| 13 | RAC Heat Pump | Yes | 8.5 | 9.0 | 20 | None | 20 | 3.6% | 0.31 | 0.33 |
| 14 | RAC Heat Pump | No | 8.0 | 8.5 | 19 | None | 19 | 3.4% | 0.28 | 0.29 |
| 15 | Subtotal: |  |  |  |  |  | 552 | Weighted EERs: | 8.77 | 9.27 |
|  | For Casement RACs the only available capacity is 8,000 Btu/hr |  |  |  |  |  |  |  |  |  |
| 26 | Casement-Only RAC | Either | (1) | 8.7 | 0 | None | 0 |  |  |  |
| 27 | Casement-Slider RAC | Either | (1) | 9.5 | 10 | Add 10 to Row 11 | 0 |  |  |  |
|  |  |  |  | Totals: | 1032 |  | 1032 |  |  |  |
| Notes: |  |  |  |  |  |  |  |  |  |  |
| (1) | Not a separate class until Oct 2000. |  |  |  |  |  |  |  |  |  |

RAC Population Weighted Mean Values

An SCE study establishes a distribution of RAC unit cooling capacity for the SCE service area as listed in Table 13.

Table 13: SCE Service Area: RAC Cooling Capacity Distribution

| Cooling Tons | BTU/hr | Percentage of Total RAC Units in SCE Service Area |
| --- | --- | --- |
| 0.5 to < 1.0 | 6,000 to <12,000 | 47% |
| 1.0 to < 1.5 | 12,000 to <18,000 | 41% |
| 1.5 to < 2.0 | 18,000 to 24,000 | 6% |
| > 2.0 | > 24,000 | 6% |

These unit cooling capacity ranges do not match Title 20 Table B-2 ( in this work paper under: 1.3 Codes & Standards Requirements Analysis) so this work paper weighted the SCE area RAC distribution evenly over the Title 20 Table B-2 requirements as follows to establish a population Weighted Mean RAC (WM-RAC).

Table 14: Basis for determining the Population Weight Mean RAC for SCE Service Area

| Population Weighted Mean RAC Capacity |  |  | Title 20 |  |  |  |  | Weighted Mean Factor BTU/hr |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BTU/hr | SCE Cooling Capacity Range BTU/ hr | % of Total RAC Units in SCE Service Area | Title 20 Cooling Capacity Range BTU/ hr | Title 20 Average Cooling Capacity BTU/ hr | Title 20: % of SCE Dist | SCE Count/ 100 RAC Units | Title 20 % Dist |  |
|  | Column (A): From Table 13 | (B): From Table 13 | (C): From | (D): Average of (C) | (E) = % of (B) | (F) = (B) * (E) *100 | (G) = (F) / 100 | (H) = (D) * (G) |
| 5000 | 6,000 to <12,000 | 47% | > 6,000 | 5000 | 14.3% | 7 | 6.7% | 336 |
| 6000 |  |  | ≥ 6,000 - 7,999 | 6500 | 28.6% | 13 | 13.4% | 873 |
| 7000 |  |  |  |  |  |  |  |  |
| 8000 |  |  | = 8,000 - 13,999 | 11000 | 57.1% | 27 | 40.5% | 4458 |
| 9000 |  |  |  |  |  |  |  |  |
| 10000 |  |  |  |  |  |  |  |  |
| 11000 |  |  |  |  |  |  |  |  |
| 12000 | 12,000 to <18,000 | 41% |  |  | 33.3% | 14 |  |  |
| 13000 |  |  |  |  |  |  |  |  |
| 14000 |  |  | ≥ 14,000 - 19,999 | 16500 | 66.7% | 27 | 29.3% | 4840 |
| 15000 |  |  |  |  |  |  |  |  |
| 16000 |  |  |  |  |  |  |  |  |
| 17000 |  |  |  |  |  |  |  |  |
| 18000 | 18,000 to 24,000 | 6% |  |  | 33.3% | 2 |  |  |
| 19000 |  |  |  |  |  |  |  |  |
| 20000 |  |  | ≥ 20,000 | 24000 | 66.7% | 4 | 10.0% | 2400 |
| 21000 |  |  |  |  |  |  |  |  |
| 22000 |  |  |  |  |  |  |  |  |
| 23000 |  |  |  |  |  |  |  |  |
| 24000 | > 24,000 | 6% |  |  | 100.0% | 6 |  |  |
| 25000 |  |  |  |  |  |  |  |  |
| 26000 |  |  |  |  |  |  |  |  |
| 27000 |  |  |  |  |  |  |  |  |
| 28000 |  |  |  |  |  |  |  |  |
| Weighted Mean RAC BTU/hr: |  |  |  |  |  |  |  | 12,906 |

For the SCE service area, the WM-RAC BTU/hr is 12,906.  The following Table 15 takes the EER Weighted Mean by Unit Design for Cooling Capacities figures from Table 11 and further weights the EERs by the Title 20 % distribution from .

Table 15: Basis for determining the Weight Mean RAC EERs for SCE Service Area

| EER Weighted Mean by Unit Design for Cooling Capacity (from Table 11) |  |  | Energy Star EER | Title 20 % Dist (from ) | Weighted Mean EER Factors |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cooling Capacity (Btu/hr) | Effective | Effective |  |  |  |  |  |
|  | 1-Jan-90 | 1-Oct-00 |  |  | Jan-90 | Oct-00 | Energy Star |
|  | Column (A) | (B) | (C) = (B) * 1.1 | (D) = : Col (G) | (E) = (A) * (D) | (F) = (B) * (D) | (G) = (C) * (D) |
| < 6,000 | 8.0 | 9.7 | 10.7 | 6.7% | 0.537 | 0.651 | 0.718 |
| ≥ 6,000 - 7,999 | 8.5 | 9.6 | 10.6 | 13.4% | 1.141 | 1.289 | 1.423 |
| ≥ 8,000 - 13,999 | 8.8 | 9.3 | 10.2 | 40.5% | 3.566 | 3.769 | 4.133 |
| ≥ 14,000 - 19,999 | 8.8 | 9.7 | 10.7 | 29.3% | 2.581 | 2.845 | 3.139 |
| ≥ 20,000 | 8.2 | 8.5 | 9.4 | 10.0% | 0.820 | 0.850 | 0.940 |
| Weighted Mean EERs: |  |  |  |  | 8.6 | 9.4 | 10.4 |

For the SCE service area, WM-RACs are 12,906 BTU/hr units that would meet EERs of 8.6 after Jan 1990, 9.4 as of Oct 2000 or an Energy Star rating of at least 10.4.

Energy Savings for WM-RAC

Table 16 below lists the SCE climate zones and repeats the SEvwm Weighted Slope and YEvwm Weighted Y Intercept from Table 8.  Using Equation (6), Columns (C), (D) and (E) show the resulting energy savings calculations for WM-RACs for Jan 1990 code, Oct 2000 code and Energy Star (10% above Oct 2000 code) for the SCE climate zones.  Column (F) numbers are the total energy savings of upgrading from a Jan 1990 Code to Energy Star WM-RAC.  Column (G) numbers are the energy savings for buying an Energy Star WM-RAC instead of a current (Oct 2000) C-RAC: the energy savings for this work paper.  Column (H) is the energy savings for replacing an existing Jan 1990 code RAC with a C-RAC: the energy savings for the RAC Recycling work paper.

Table 16: WM-RAC Annual Energy Savings (AES)

| For Weighted Means RAC: |  | BTU/ hr: | 12,906 | Weighted Means EERs |  |  | WM-RAC Energy Star AES less: (kWh/Unit) |  | Code Dif-ferential AES: Oct 2000 less Jan 1990 (kWh/Unit) (Note 2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 8.6 | 9.4 | 10.4 |  |  |  |
| DEER Values |  | Annual Energy Savings (AES): (From Table X) |  | WM-RAC Total AES: (kWh/WM RAC) |  |  |  |  |  |
| Climate Zone City | CA T24 CZ: | SEvwm Weighted Slope | YEvwm Weighted Y Intercept | Code: Jan 1990 | Code: Oct 2000 | Energy Star | Code: Jan 1990 | Code: Oct 2000 (Note 1) |  |
|  |  | Column (A) | (B) | (C) (Note 3) | (D) (Note 4) | (E) (Note 5) | (F) = (E) - (C) | (G) = (E) - (D) | (H) = (F) - (G) |
| Long Beach | 6 | 183.835 | -1,297.400 | 305.0 | 463.2 | 660.9 | 355.9 | 197.7 | 158.2 |
| El Toro | 8 | 229.651 | -1,624.025 | 377.5 | 575.1 | 822.1 | 444.6 | 247.0 | 197.6 |
| Burbank | 9 | 216.026 | -1,537.142 | 344.9 | 530.8 | 763.1 | 418.2 | 232.3 | 185.9 |
| Riverside | 10 | 204.380 | -1,458.538 | 321.7 | 497.6 | 717.4 | 395.7 | 219.8 | 175.8 |
| Fresno | 13 | 202.615 | -1,423.334 | 343.3 | 517.6 | 735.5 | 392.2 | 217.9 | 174.3 |
| China Lake | 14 | 187.204 | -1,323.838 | 307.7 | 468.8 | 670.1 | 362.4 | 201.3 | 161.1 |
| El Centro | 15 | 272.872 | -1,912.036 | 467.5 | 702.3 | 995.7 | 528.3 | 293.5 | 234.8 |
| Mt. Shasta | 16 | 147.093 | -1,033.533 | 248.9 | 375.5 | 533.7 | 284.8 | 158.2 | 126.6 |
| Notes: | (1) | Energy Star RAC energy savings: Purchase an Energy Star Unit instead of an Oct 2000 Code Unit. |  |  |  |  |  |  |  |
|  | (2) | Residential RAC Recycling energy savings: Recycle a Jan 1990 Code Unit and replace with an Oct 2000 Code Unit. |  |  |  |  |  |  |  |
|  | (3) | (C) = ((B) + (A) * 8.6) / (12,000 / 12,906) |  |  |  |  |  |  |  |
|  | (4) | (D) = ((B) + (A) * 9.4) / (12,000 / 12,906) |  |  |  |  |  |  |  |
|  | (5) | (E) = ((B) + (A) * 10.4) / (12,000 / 12,906) |  |  |  |  |  |  |  |

Example 4 - Table 14 Calculations

As an example, the equation to determine the total annual energy savings for an RAC with a BTU/hr capacity of 12,906 and EER of 8.6 in the Long Beach climate zone is:

YEa = (YEvwm + SEvwm * Xa) * (WM-RAC Capacity (BTU/hr) / 12,000 ((BTU/hr)/Cooling Ton)

YEa = (-1,297.400 (kWh / Cooling Ton year)
+183.835((year-kWh/Cooling Ton year) / (BTU/W))*8.6(BTU/W)) 
* 12906(BTU/hr)/(WM-RAC Unit)) / (12000((BTU/hr)/(Cooling Ton))

YEa = 305.0 kWh / year WM-RAC Unit

Averaging the last three columns of Table 16 produces average annual energy savings for the Residential RAC Recycling and Energy Star RAC work papers and a combined total savings as shown in Table 17.  The total savings is comparable to the RAC energy savings from the LIEE program of PY 2001.

Table 17: Average Annual Energy Savings for a WM-RAC

| For a WM-RAC rated at 12,906 Btu: | Average Annual Energy Savings (kWh/WM-RAC): |
| --- | --- |
| Residential RAC Recycling: Replace a Jan 1990 Code Unit with an Oct 2000 Code Unit | 176.8 |
| Energy Star RAC: Purchase an Energy Star Unit instead of an Oct 2000 Code Unit | 221.0 |
| Total Savings: Replace a Jan 1990 Code Unit with an Energy Star Unit | 397.7 |

## 2.2. Demand Reduction Estimation Methodologies

To derive the demand reduction, this work paper uses the Weighted Mean RAC of 12,906 Btu.  The equation for EER is:

EER = Cooling Capacity (Btu/hr) / Power(Watts)

To determine Power in kW:

Power (kW) = [Cooling Capacity (Btu/hr) / EER] * [1 (kW) / 1000 (Watts)]

Power and Demand Reduction for the Weighted Mean EERs are shown in the following table:

Table 18: Weighted Mean RAC Demand Reduction

| For Weighted Mean RAC 12,906 Btu / hr |  |  |  |
| --- | --- | --- | --- |
|  | Code: Jan 1990 | Code: Oct 2000 | Energy Star |
| EER | 8.6 | 9.4 | 10.4 |
| Power (kW) | 1.501 | 1.373 | 1.241 |
| Demand Reduction (kW) |  |  |  |
| Energy Star - Code: Oct 2000 (1): |  |  | 0.132 |
| Code: Oct 2000 - Code: Jan 1990 (2): |  |  | 0.128 |
| Notes: | (1) Energy Star RAC Demand Reduction: Purchase an Energy Star Unit instead of an Oct 2000 Code Unit. |  |  |
|  | (2) Residential RAC Recycling Demand Reduction: Recycle a Jan 1990 Code Unit and replace with an Oct 2000 Code Unit. |  |  |

The Energy Star demand reduction is 0.132 kW for all climate zones in SCE’s service area.  This is based on the assumption that for a typical summer three day heat wave peak demand period RACs will operate at or above the 10 CFR Section 430.23(f) (2005) test condition of 95°F.  As a result, the peak demand would be close to the same value for all units across different climate zones.  This assumption simplifies the demand estimation process and also reduces any discrepancies due to under estimation of the potential demand reduction.

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio.  The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved.  For electricity, the avoided cost varies hourly over an entire year.  Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year.  The distribution of savings over the year is represented by the measure’s load shape.

The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year.  An hourly load shape indicates what fraction of annual savings occurs for each hour of the year.  A TOU load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff.  Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period.  Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Case Load Shapes

The existing base case RAC energy use and peak demand load shapes would follow typical air conditioner hourly demand profile.  Seasonal variations should follow the typical seasonal outdoor dry-bulb temperature variation for each climatic zone over a course of a year.  The Load Shapes for this work paper are AC_Cooling-RC which is inclusive of both building type and climate zone.

## 3.2 Measure Load Shapes

The RAC measure would move the typical RAC hourly demand profile lower in all times except when load is zero when compared to the base system.  Figure 2 and Figure 3 represent the TOU End Use Energy and Peak Demand factors for air conditioning: cooling RC measures that are embedded within the SCE E3 Calculator.

0%

5%

10%

15%

20%

25%

30%

35%

TOU Share (%)

TOU %

32%

20%

28%

10%

11%

Smr On

Smr Ptl

Smr Off

Wtr Ptl

Wtr Off

Figure 2: TOU AC Cooling-RC Energy Share

0%

20%

40%

60%

80%

100%

TOU Peak Relative to Summer Peak

Peak Ratio

100%

91%

36%

9%

9%

Smr On

Smr Ptl

Smr Off

Wtr Ptl

Wtr Off

Figure 3: TOU Peak kW Factors

# Section 4. Base Case & Measure Costs

- The only difference in costs between the base case and measure costs would be for the greater cost of ES-RAC units over C-RAC units that simply meet Federal and State appliance standards.  Other costs such as installation labor and materials are assumed to be identical.  This work paper uses WM-RAC of 12,906 BTU/hr and provides average costs sourced from Consumer Reports Magazine for 9,800 to 12,500 BTU/hr units which may under price an actual WM-RAC unit.

## 4.1 Base Case Costs

The base case costs are the purchase prices of C-RAC units that meet minimum Federal and State of California appliance standards.  Base costs are estimated at $295.00.

## 4.2 Measure Costs

The measure costs are the greater cost of ES-RAC units that exceed the Federal EER appliance standards by at least 10%.  Measure costs are estimated at $376.00.

## 4.3 Incremental & Full Measure Costs

The only cost differences are the extra capital costs of purchasing an Energy Star unit over a non-energy star unit.  Thus the incremental cost is estimated at $81.00.  Installation costs are presumed to be identical.  To determine the full measure costs, this work paper presumes customers will self install RAC units and therefore the Full Measure cost is estimated at $376.00.

# Appendices

# Appendix A: RAC EER Design Variance Weighted Mean

| RAC Design Variance EER Merge |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Cells in Blue Arial font are from Title 20 Table B-2 |  |  |  | Energy Star Product Search Unique Units (UU) |  |  |  | EER Weighted Mean Factors by Unit Design for Capacity |  |
| Row: | Appliance | Louvered Sides | Minimum EER |  |  |  |  |  |  |  |
|  |  |  | Effective Jan 1990 | Effective Oct 2000 | No. of UUs | Adjust-ments to equiv. EERs | Adjust-ed No. of UUs | % of UUs per Cap | Effective Jan 1990 | Effective Oct 2000 |
|  | Column (A) | (B) | (C) | (D) | (E) | (F) | (G) = (E)+(F) | (H) = (G)/ Subtotal | (I) = (C)*(H) | (J) = (D)*(H) |
|  | For Capacities < 6,000 Btu/hr |  |  |  |  |  |  |  |  |  |
| 1 | RAC | Yes | 8.0 | 9.7 | 123 | None | 123 | 99.2% | 7.9 | 9.6 |
| 2 | RAC | No | 8.0 | 9.0 | 1 | None | 1 | 0.8% | 0.1 | 0.1 |
| 3 | RAC Heat Pump | Yes | 8.5 | 9.0 | 0 | None | 0 | 0.0% | 0.0 | 0.0 |
| 4 | RAC Heat Pump | No | 8.0 | 8.5 | 0 | None | 0 | 0.0% | 0.0 | 0.0 |
| 5 | Subtotal: |  |  |  |  |  | 124 | Weighted EERs: | 8.0 | 9.7 |
|  | For Capacities ≥ 6,000 - 7,999 Btu/hr |  |  |  |  |  |  |  |  |  |
| 6 | RAC | Yes | 8.5 | 9.7 | 98 | None | 98 | 90.7% | 7.7 | 8.8 |
| 7 | RAC | No | 8.5 | 9.0 | 8 | 2 from Row 10 | 10 | 9.3% | 0.8 | 0.8 |
| 8 | RAC Heat Pump | Yes | 8.5 | 9.0 | 2 | Add 2 to Row 9 | 0 | 0.0% | 0.0 | 0.0 |
| 9 | RAC Heat Pump | No | 8.0 | 8.5 | 0 | None | 0 | 0.0% | 0.0 | 0.0 |
| 10 | Subtotal: |  |  |  |  |  | 108 | Weighted EERs: | 8.5 | 9.6 |
|  | For Capacities ≥ 8,000 - 13,999 Btu/hr |  |  |  |  |  |  |  |  |  |
| 11 | RAC | Yes | 9.0 | 9.8 | 310 | 10 from Row 27 | 320 | 58.0% | 5.2 | 5.7 |
| 12 | RAC | No | 8.5 | 8.5 | 193 | None | 193 | 35.0% | 3.0 | 3.0 |
| 13 | RAC Heat Pump | Yes | 8.5 | 9.0 | 20 | None | 20 | 3.6% | 0.3 | 0.3 |
| 14 | RAC Heat Pump | No | 8.0 | 8.5 | 19 | None | 19 | 3.4% | 0.3 | 0.3 |
| 15 | Subtotal: |  |  |  |  |  | 552 | Weighted EERs: | 8.8 | 9.3 |
|  | For Capacities ≥ 14,000 - 19,999 Btu/hr |  |  |  |  |  |  |  |  |  |
| 16 | RAC | Yes | 8.8 | 9.7 | 143 | None | 143 | 94.7% | 8.3 | 9.2 |
| 17 | RAC | No | 8.5 | 8.5 | 3 | None | 3 | 2.0% | 0.2 | 0.2 |
| 18 | RAC Heat Pump | Yes | 8.5 | 9.0 | 5 | None | 5 | 3.3% | 0.3 | 0.3 |
| 19 | RAC Heat Pump | No | 8.0 | 8.0 | 0 | None | 0 | 0.0% | 0.0 | 0.0 |
| 20 | Subtotal: |  |  |  |  |  | 151 | Weighted EERs: | 8.8 | 9.7 |
|  | For Capacities ≥ 20,000 Btu/hr |  |  |  |  |  |  |  |  |  |
| 21 | RAC | Yes | 8.2 | 8.5 | 92 | None | 92 | 94.8% | 7.8 | 8.1 |
| 22 | RAC | No | 8.2 | 8.5 | 0 | None | 0 | 0.0% | 0.0 | 0.0 |
| 23 | RAC Heat Pump | Yes | 8.5 | 8.5 | 5 | None | 5 | 5.2% | 0.4 | 0.4 |
| 24 | RAC Heat Pump | No | 8.0 | 8.0 | 0 | None | 0 | 0.0% | 0.0 | 0.0 |
| 25 | Subtotal: |  |  |  |  |  | 97 | Weighted EERs: | 8.2 | 8.5 |
|  | For Casement RACs the only available capacity is 8,000 Btu/hr |  |  |  |  |  |  |  |  |  |
| 26 | Casement-Only RAC | Either | (1) | 8.7 | 0 | None | 0 |  |  |  |
| 27 | Casement-Slider RAC | Either | (1) | 9.5 | 10 | Add 10 to Row 11 | 0 |  |  |  |
|  | Total for all Capacities: |  |  |  | 1032 |  | 1032 |  |  |  |
| Notes: |  |  |  |  |  |  |  |  |  |  |
| (1) | Not a separate class until Oct 2000. |  |  |  |  |  |  |  |  |  |

Index

A

Above Code Savings	10

AHAM	11

Air Conditioner

Appliance Efficiency Regulations Definition	7

Air Source Heat Pump

Appliance Efficiency Regulations Definition	7

Appendix A - RAC EER Design Variance Weighted Mean	26

Appliance Efficiency Regulations

Title 20	7

Appliance Efficiency Regulations Definition

PTAC	7

Room Air Conditioning Heat Pump	8

SEER	8

Appliance Efficiency Regulations Definition

Air Conditioner	7

Air Source Heat Pump	7

Btu	7

Casement Window	7

Casement-Only Room Air Conditioner	7

Casement-Slider Room Air Conditioner	7

Coefficient of Performance	7

Cooling Capacity	7

EER	7

Heat Pump	7

Packaged Terminal Air Conditioner	7

Appliance Efficiency Regulations Definition

Packaged Terminal Heat Pump	7

Appliance Efficiency Regulations Definition

Room Air Conditioner	7

At a Glance Summary	i

Average Annual Energy Savings for a WM-RAC Table	23

B

Base Case & Measure Costs	25

Base Case Description

DEER Calcs	13

Base Case for Savings Estimates

EM&V, Market Potential, and Other Studies	10

Net-to-Gross Ratios for Different Program Strategies	11

Base Case Load Shapes	24

Base Cases and Measure Effective Useful Lives

EM&V, Market Potential, and Other Studies	11

Basis for Determining Population Weight Mean RAC for SCE Service Area Table	20

Basis for Determining Weight Mean RAC EERs for SCE Service Area Table	21

Btu	13

Appliance Efficiency Regulations Definition	7

C

Calculation Methods	12

Demand Reduction Estimation Methodologies	23

Energy Savings Estimation Methodologies	13

Example 1 - LSLR Method for Equations	14

Example 2 - Vintage Weighted Mean Equation	16

Example 3 - RAC EER Design Variance Weighted Mean Values	18

Example 4 - Table 14 Calculations	22

Casement Window

Appliance Efficiency Regulations Definition	7

Casement-Only Room Air Conditioner

Appliance Efficiency Regulations Definition	7

Casement-Slider Room Air Conditioner

Appliance Efficiency Regulations Definition	7

CEUS	15

NLOCS	15

Codes & Requirements Analysis	7

Codes & Standards Requirements Analysis

Definitions	7

PTAC Requirements	9

RAC Requirements	8

Coefficient of Performance

Appliance Efficiency Regulations Definition	7

Cooling Capacity

Appliance Efficiency Regulations Definition	7

Costs

Base & Measure	25

Base Case	25

Incremental & Full Measure	25

Measure	25

C-RAC	5

CTon	14

Customer Savings	10

D

Data

Baseline	5

General Measure	5

DEER	5

DEER Calcs	12

Base Case Description	13

ECImpact	13

EImpact	13

DEER Differences Analysis	5

DEER Table

PTAC EER Values for Lodging - Motel	6

DEER Table 6-1 (Partial) Non-residential Space Characteristics	6

DEER Table 6-2 (Partial) Non-residential Prototype Descriptions	6

Definitions	7

Demand Reduction Estimation Methodologies

Calculation Methods	23

Demand Reductions

Rev 0-to-1 Comparison	ii

Document Revision History	ii

Document Summary	i

DoE	5

E

ECImpact

DEER Calcs	13

EER	10

Appliance Efficiency Regulations Definition	7

EER Weighted Mean by Unit Design for Cooling Capacity Table	18

EImpact

DEER Calcs	13

EM&V, Market Potential, and Other Studies	9

Base Case for Savings Estimates	10

Base Cases and Measure Effective Useful Lives	11

Energy Efficiency Policy Manual	11

Energy Efficiency Ratio

Appliance Efficiency Regulations Definition	7

Energy Savings

Rev 0-to1 Comparison	ii

Energy Savings Estimation Methodologies

Calculation Methods	13

Energy Savings for WM-RAC	21

LSLR Method for Equations	13

RAC EER Design Variance Weighted Mean Values	17

Vintage Weighted Mean Equations	15

Weighted Mean Values	19

Energy Star	5

Energy Star Energy Efficiency Ratio Requirements Table	11

EPA	5

ES-RAC	5

EUL	11

Example 2 - Climate Zone 6 Vintage Weighted Mean Linear Slope Calculations	16

Example 2 - Climate Zone 6 Vintage Weighted Mean Y Intercept Calculations	17

Example 3 - RAC Design Weighted Mean Values	19

G

General Measure & Baseline Data

Codes & Standards Requirements Analysis	7

Measure Description & Background	5

General Measure and Baseline Data	5

DEER Differences Analysis	5

EM&V, Market Potential, and Other Studies	9

H

Heat Pump

Appliance Efficiency Regulations Definition	7

I

Index	28

L

LIEE	10

List of Figures	iv

List of Tables	iv

Load Shapes	23

Base Case	24

Measure Load	24

LSLR Method	5

LSLR Method for Equations

Calculation Methods	13

M

Measure Load Shapes	24

TOU AC Cooling-RC Energy Share Graphic	24

TOU Peak kW Factors Graphic	25

Motel Lodging Guest Rooms	5

N

Net-to-Gross	11

Net-to-Gross Ratios for Different Program Strategies

Base Case for Savings Estimates	11

Net-to-Gross Ratios Table	12

New Construction	11

NFO	11

Nonresidential Compliance Manual For California's 2005 Energy Efficiency Standards

Title 24	13

P

Packaged Terminal Air Conditioner

Appliance Efficiency Regulations Definition	7

Packaged Terminal Heat Pump

Appliance Efficiency Regulations Definition	7

peak demand period	23

PT units	5

PTAC	5

Appliance Efficiency Regulations Definition	7

PTAC Requirements	9

PTHP	5

R

RAC	5

RAC EER Design Variance Weighted Mean	26

RAC EER Design Variance Weighted Mean Values

Calculation Methods	17

RAC Requirements	8

RASS	9

References	31

Replace on Burnout	11

ROB	11

Room Air Conditioner

Appliance Efficiency Regulations Definition	7

Room Air Conditioners and Room Air Conditioning Heat Pump

Section 1605.1 (b) Definition	8

Room Air Conditioning Heat Pump

Appliance Efficiency Regulations Definition	8

S

SCE	9

SCE Rebate Scale	13

SCE Service Area

RAC Cooling Capacity Distribution Table	19

Scoping Study	10

Section 1605.1 (2)

Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps	9

Section 1605.1 (2) Table B-3 Standards for Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps	9

Section 1605.1 (b)

Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps	8

Room Air Conditioners and Room Air-Conditioning Heat Pumps	8

Section 1605.1 (b) Definition

Room Air Conditioners and Room Air Conditioning Heat Pump	8

Section 1605.1 (b) Table B-2 Standards for Room Air Conditioners and Room Air-Conditioning Heat Pumps	8

SEER	5

Appliance Efficiency Regulations Definition	8

Standards for Packaged Terminal Air Conditioners and Packaged Terminal Heat Pumps	9

Standards for Room Air Conditioners and Room Air-Conditioning Heat Pumps	8

T

Table of Contents	iii

Title 20

Appliance Efficiency Regulations	7

Title 24

Nonresidential Compliance Manual For California's 2005 Energy Efficiency Standards	13

TOU	5

TOU AC Cooling-RC Energy Share	24

TOU Peak kW Factors	25

TRC	24

U

UEC	9

V

Vintage Weighted Mean Equations

Calculation Methods	15

Vintage Weighted Mean Slopes & Y Intercepts	16

W

Weighted Mean Values

Calculation Methods	19

WM-RAC	10, 20

Energy Savings Calculations	21

WM-RAC Annual Energy Savings Table	22

WM-RAC Demand Reduction Table	23

# References

.	“History”, Energy Star website (http://www.energystar.gov/index.cfm?c=about.ab_history)

.	“Major Milestones”, Energy Star website (http://www.energystar.gov/index.cfm?c=about.ab_milestones)

.	“Room Air Conditioners”, Energy Star website (http://www.energystar.gov/index.cfm?c=roomac.pr_room_ac)

.	“2004-2005 Database for Energy Efficiency Resources (DEER) Update Study”, Prepared for SCE by Itron, Inc., Dec 2005, Section 6: Page 6-4.

.	Ibid: Note Error: Reference source not found, Section 6: Page 6-10.

.	Table: “Cooling Load Check Figures”, ASHRAE Pocket Guide for Air Conditioning Heating Ventilation Refrigeration (Inch-Pound Edition), ASHRAE, 1993, Page 128

.	Ibid: Note Error: Reference source not found: Data from Page 6-19 DEER HVAC System Properties workbook (DEER HVAC System Properties-051212.xls) Tab: DX HVAC System Baseline: Msr: 99.

.	Appliance Efficiency Regulations CEC-400-2005-012, California Energy Commission, April 2005, State of California Code Of Regulations, Title 20: Division 2, Chapter 4, Article 4, pages 11 thru 13.

.	Ibid: Note Error: Reference source not found, pages 73 & 74.

.	Ibid: Note Error: Reference source not found, pages 74 & 75.

.	California Statewide Residential Appliance Saturation Study Update to Air Conditioning Unit Energy Consumption Estimates Using 2004 Billing data – June 2006 CEC-400-2006-009, Table 9 & 10 page 21

.	Ibid: Note Error: Reference source not found, page 17.

.	Ibid: Note Error: Reference source not found, page 132.

.	Ibid: Note Error: Reference source not found, page 7.

.	SCE Residential Room Air-Conditioner Recycling Scoping Study, page 2.

.	“Table 3-8 SCE LIEE Program Impact Estimates for PY-2001”, Impact Evaluation Of The 2001 Statewide Low-Income Energy Efficiency (LIEE) Program - Final Report  Volume 2  Study ID Number 577, Prepared for SCE, SC Gas Co., SDG&E and PG&E, Prepared by KEMA-XENERGY Inc.; Oakland, California and Business Economic Analysis & Research; Lemon Grove, California, April 8, 2003, Page E-6 (http://www.calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf)

.	“Room Air Conditioners”, Energy Star website (http://www.energystar.gov/index.cfm?c=roomac.pr_crit_room_ac)

.	“Table 6 : Comparison of Service Life Estimates”, 2007 ASHRAE Handbook-HVAC Applications (Inch-Pound Edition), ASHRAE, 2007, Page A36.3

.	“Average Useful Life of Major Home Appliances”, National Family Opinion, Inc. (NFO), 1996 Survey (http://www.aham.org/industry/ht/action/GetDocumentAction/id/5271)

.	Ibid: Note Error: Reference source not found: Source data for Table of DWWAGE by WWADD

.	2004-05 Database for Energy Efficiency Resources (DEER), Version 2.01 October 26, 2005.  Net-to-Gross Ratios Table, at (http://eega.cpuc.ca.gov/deer/Ntg.asp)

.	RAC Calcs.zip: DEER Measure D03-099 Lodging-Motels.xls: Sheet “DEER Cals” (RAC Calcs.zip)

.	Ibid: Note Error: Reference source not found, Sheet “DEER Hourly Profiles-MTL”

.	Current requirements only: Nonresidential Compliance Manual For California's 2005 Energy Efficiency Standards (Title 24), California Energy Commission, Publication Number: CEC-400-2005-006-CMF, Dated Published: April 2005, Effective Date: October 1, 2005.

.	Ibid: Note Error: Reference source not found, Sheet “LSLR Method & Vintage Weighing”

.	Ibid: Note Error: Reference source not found, Sheet “LSLR Method Example+Graph”

.	CEUS (SCE CEUS based Nonres Vintage & CZ Distributions.xls)

.	Ibid: Note Error: Reference source not found, Sheet “LSLR Method & Vintage Weighing”

.	Ibid: Note Error: Reference source not found, Sheet “DEER Measure D03-099 Lodging-Motels.xls”.

.	Ibid: Note Error: Reference source not found.

.	Ibid: Note Error: Reference source not found.

.	“Find ENERGY STAR Qualified Room Air Conditioners”, Energy Star website (http://www.energystar.gov/index.cfm?fuseaction=roomac.search_room_air_conditioners)

.	RAC Calcs.zip: Energy Star RACs-20070802.xls: Sheet “EER Weighting by Unique Units”. (RAC Calcs.zip)

.	Ibid: Note Error: Reference source not found: Sheet “Energy Star Product Listing”.

.	Ibid: Note Error: Reference source not foundError: Reference source not found: “Figure 1: RAC Cooling Capacity in Tons”

.	Ibid: Note Error: Reference source not found: E3 WM-RAC Weighting Calcs.xls Sheet: “Weighted Mean RAC and EERs”.

.	Ibid: Note Error: Reference source not found.

.	Ibid: Note Error: Reference source not found: Sheet: “WM-RAC Energy Savings”.

.	Ibid: Note Error: Reference source not found.

.	Ibid: Note Error: Reference source not found.

.	Final Report Load Shape Update Initiative, KEMA Inc. with the assistance of JJ Hirsch and Associates and Itron Inc., prepared for the California Public Utilities Commission under contract to PG&E, November 15, 2006, Revised November 17, 2006, page 2-1.

.	SCE Demand Side Management Unit Energy Savings, Energy Efficiency & Market Services, Engineering Analysis & Development, Revision 1, October 1, 1992, page 184.

.	Table “Ratings Air Conditioners”, Consumer Reports Magazine, July 2007, page 51.

.	RAC Calcs.zip: Consumer Reports Mag-Jul 2007-pg 51 Partial Table.xls.

.	Ibid: Note Error: Reference source not found.