## VM 19 - Outage Summary
Textbox13 | Textbox14 | VMACD | CIRCUITNUMBER | NEARESTADD | DM_SPECIES | OTGDATE | FACILITYID | Textbox31 | CAUSECODE_1 | CAUSECODE | PROPERTYTYPE | FACTTYPE | LASTCLEARANCEPI | POSSCAUSE | LASTPIDATE | OTGAVOIDABLE | LASTCLEARANCETRIM | OTGFIREASSOCIATED | LASTTRIMDATE | OTGPRECOMPLIANCE | TREEHEIGHT | LINECLEARANCE | DM_DBH | RESP_PARTY | TREEBASE_LINEDIST | RESP_CONTRCTR | REFUSALDATE | TREEDEFECTS | REFUSALWOID | TREEDEFECTS_2 | TREEDEFECTS_3 | OTGTREEUNHEALTHY | OTGCAUSECOMMENT | OTGRESIDENTCOMMENT | OTGRECOMMEND | Textbox406 | OTGINVESTIGATIONDT
OUTAGE ID NUMBER: 150006E82894s | DISTRICT NAME: | 212 | 546 | 3888 RIVIERA DR, SAN DIEGO 92109 | Palm-Fan | 2015-11-16 | GF240 | P193922 P193922 | 428 - Palm tree contact due to storm/wind | 428 - Palm tree contact due to storm/wind | Private | Primary | 0.0 to 2.0 ft | Tree Growth | 2014-12-03 | Y | 10.0 to 11.9 ft | N | 2014-12-30 | Y | 30.1 to 40 ft | 2.1 to 4.0 ft | 13.0 to 17.9 in | None | 6.1 - 8 |  |  | None |  | No Record | No Record | N | The top (whole crown) of an inventory Mex Fan Plam was blown into riser pole fuses in high winds and rain causing one fuse to blow. Line was de-energized and tree crew was called out to safely clear palm in storm event. Tree was topped clear 11-16-15. | Property Mangement Company Riviera Villages (Theresa Rameriz 855.550.0220) was contacted and removal opffered for this and one other MFP that will become an issue 3-5 years from now. | Property Mnagement Company would only allow authorization for removing the one Mex Fan that was topped on 11-16-15 storm call out. Area Forester declined and will only remove this toppped tree if the second MFP (future problem) was also removed. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 150115E60053s | DISTRICT NAME: | 652 | 63 | 16835 EL CAMINO REAL, RANCHO SANTA FE 92067 | Eucalyptus | 2015-01-15 03:44 | BF635 | P410890 P410891 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2014-11-05 | N | 10.0 to 11.9 ft | N | 2015-01-05 | Y | 0.0 to 5.0 ft | 10.0 to 11.9 ft | 42.0 to 47.9 in | None | 20.1 - 30 |  |  | Root Rot |  | No Record | No Record | Y | Tree failure due to root decay. Large Eucalyptus fell over in calm weather conditions. Tree may have had some lean towards the facilities that would have caused the outage with diminished root system | Neighbors said there was no wind or weather that would have caused the tree to fall | Several other trees in the vicinity were inspected and removed the day of the outage. With seveal more to be scrutinized and evaluated within the week | 2020-03-20 14:20 | 2015-01-16
OUTAGE ID NUMBER: 150120E60309s | DISTRICT NAME: | 220 | 701 | 8537 GLENHAVEN ST, SAN DIEGO 92123 | Eucalyptus | 2015-01-20 | AI2016 | P92872 P92873 | 704 - Line fault/tree trimming | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 4.1 to 5.9 ft | Non-SDGE Crew Caused | 2014-12-30 | Y | 10.0 to 11.9 ft | N | 2014-04-02 | N | 60.1 to 80 ft | 4.1 to 5.9 ft | 24.0 to 35.9 in | Other | 12.1 - 15 | No Record |  | None |  | No Record | No Record | N | A private third party contractor was working on removing inventory Eucalyptus AI2016. California Tree Service (760-510-8100). During the process, it is speculated, that a limb made contact with SDG&E facilities. It is not known if it where direct or indirect contact with primary wires. No injuries were reported. Fuse at P92009 blew at the same time this crew was working the tree. Responding ETS only saw tree company working in nearby trees. | Area Forester was contacted and arrived on scene. The Forester saw California Tree Service crews working inventory Eucalyptus AI2016 on day of reported outage 1-20-15 and engaged tree crews on site. The crews did not admit causing the outage, but admit hitting / "brushing" facilities incedently. Area Forester on scene witnessed very large limbs being roped down near SDG&E primary wires, making contact with service drops and guy wires. It is speculated that there may have been enough force on any one of the large size limbs that were removed earlier, to hit service drops and , or guy wires with enough force to cause primary wires to slap together in, or around the span they were working on. Responding BC ETS concurred that this might have been the cause as well. | Area Forester made contqact with Ca Tree Service supervision (not on site) in an effort to assist this private company in safely working large trees near SDG&E facillties. Arrangements were made to have SDG&E tree trim contractor to clear Eucs to greater then 10ft / make safe two remaining trees, including this one, on the property that were assigned to this company for removals. Utiltiy Tree Service was dispatched next day 1-22-15. Trees were safely cleared. | 2020-03-20 14:20 | 2015-02-02
OUTAGE ID NUMBER: 150126E60786s | DISTRICT NAME: | 398 | 231 | 4701 SAN JACINTO TER, FALLBROOK 92028 | Palm-Fan | 2015-01-26 | ON661 | P414987 P414988 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2014-03-04 | Y | 10.0 to 11.9 ft | N | 2013-05-15 | N | 60.1 to 80 ft | Unable to Verify | 13.0 to 17.9 in | None | 6.1 - 8 | No Record |  | Dead Branch |  | Weak Branch Attachment | No Record | N | This tall Fan Palm directly adjacent to the primary released dead Palm fronds during a storm event and contacted the facilities bringing down the lines. Several fronds were lying across the street in the grass which indicated fronds had been falling from this tree, and through the primary, for quite some time. This outage was preventable because the tree was not listed for prune when it should have been. The tree was listed PIC by PI but had been pruned the year before. DRG reported that the PI had made a mistake and “misclicked” the improper Condition Code and had intended to have this tree pruned and for the Condition Code to be PIP. | There was no one home. | This and 2 other Palms were secured for removal. The DRG Account Manager will review this situation with the PI Team and stress the need to double check the Condition Code before exiting the asset when listing trees. | 2020-03-20 14:20 | 2015-01-27
OUTAGE ID NUMBER: 150202E61455s | DISTRICT NAME: | 610 | 505 | 591 VALE VIEW DR, VISTA 92083 | Eucalyptus | 2015-02-02 | FF6896 | P114303 P114302 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2014-12-17 | N | 10.0 to 11.9 ft | N | 2012-03-27 | N | 60.1 to 80 ft | Unable to Verify | 36.0 to 41.9 in | None | 8.1 - 10 | No Record |  | Root Rot |  | Co-dominant Branch | No Record | Y | This large Euc failed at the roots and brought down the conductors. The tree was a multiple trunk of 3 dividing at the ground level and these types of codominant stems are highly-prone to failure. The outage was non-preventable with lots of root rot and punky wood at the base below the soil line that was not visible. | No one was home. | I had Davey make safe the remaining portions of the tree still standing and I have a voicemail into the property owner to discuss this and other tree issues on the property. | 2020-03-20 14:20 | 2015-02-03
OUTAGE ID NUMBER: 150504E68325s | DISTRICT NAME: Eastern | 454 | 357 | 2024 VIA TRUENO, ALPINE 91901 | Birch | 2015-05-04 | QN261 | P972747 P972748 | 312 - Flashover/vegetation | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2014-12-16 | N |  | N |  | Y | 20.1 to 30.0 ft | 10.0 to 11.9 ft | 8.0 to 12.9 in | None | 20.1 - 30 |  |  | None |  | None | None | N | According to 05-04-15 DSOR, responding ETS found "branch across bushing of Sta# 357-577 on P972747" and code the outage as tree vegetation contact cause. Area Forester investigates outage in the field on 5-7-15. A very small piece of vegetation (1/8" x 24" Birch twig) with burn marks was found at base of pole P972747 (with in the 10ft brushed circle of subject pole). Most likely scenerio was the vegetation detached from nearest Birch tree (inventory QN261), located mid-span about 10ft to side of conductors and approximately 160ft from pole P972747. The twig most likely was blown onto primary conductor, then slid up conductor by light winds to the nearby transformer mounted on Pole P972747 where it cross phased at the transformer jumpers causing the outage. Primary jumpers are estimated to be about 8" apart here on pole P972747 at transformer. According to Alpine area weather reports for 5-4-15, there was light rain and light winds blowing from the Southwest at the time of the outage. This matches up to the location of the Birch tree and the speculation that a small piece of vegeation could have been pushed up the wire approximately 160ft toward the transformer pole where reponding ETS found it to be the cause of the outage. | Outage time was 2:22am. No witnesses. | All trees in the area were inspected by Area Forester and are clear and compliant. no follow up tree trim required. | 2020-03-20 14:20 | 2015-05-07
OUTAGE ID NUMBER: 150531E70373 | DISTRICT NAME: | 395 | 350 | 30656 DIAZ RD, VALLEY CENTER 92082 | Eucalyptus | 2015-05-31 | TZ766 | P516217 P816515 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2014-08-07 | N | 10.0 to 11.9 ft | N | 2013-09-12 | Y | 20.1 to 30.0 ft | 12.0 to 14.9 ft | 13.0 to 17.9 in | None | 15.1 - 20 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | A small "flyer" from a nearby Euc (non-inventory) blew onto the primary conductor or pole and caused the outage. The ETS (Dan Doyle 760 497-1590) said he found a small branch and knocked it off the pole but I could not find it. I did find the small branch on the pole that is in the attached pics. It may have been an additional limb that blew there. I called Station Y to dispatch an ETS to remove the branch. | None | No further work, outside of routine compliance pruning, is required at this site. | 2020-03-20 14:20 | 2015-06-02
OUTAGE ID NUMBER: 150603E70664s | DISTRICT NAME: | 605 | 781 | 2810 ELMWOOD ST, CARLSBAD 92008 | Eucalyptus | 2015-06-03 | UX2485 | P26870 P26848 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2014-09-04 | N | 10.0 to 11.9 ft | N | 2014-12-02 | Y | 40.1 to 50 ft | Unable to Verify | 24.0 to 35.9 in | None | 20.1 - 30 | No Record |  | Root Rot |  | No Record | No Record | Y | A large over-mature Euc failed at the roots and fell into the city ROW striking the overhead conductors located across the street. No weather events or significant winds were reported by SDG&E or the property occupants. There was a heavy line-side lean present in the canopy and evidence of a grade change and soil compaction from what appeared to be the addition of a garage structure to the property and / or additional soil added to level the yard. Slate / concrete path stones were unearthed due to the root failure and exposed them several inches below the current soil grade indicating there was a pathway there some time ago. With this change in grade, a long-term drought in Southern California, and possibly the addition of a garage structure / grade change near the root base, a white fungus began compromising the root system predominantly on the back side of this leaning tree (line / street side lean) where the compaction was present. White funguses can typically thrive in dryer, anaerobic (compacted) soil conditions. The fungus eventually weakened the larger root structures and they failed, bringing the tree down. There was no fire to report, only damage to the street asphalt from the arching of the conductor. | An interview with the tenant (a vacation renter from Denver, Colorado) revealed little other than she heard loud cracking before the tree failed and then the arching of the conductor. She (Alicia Garcia 213 221-5566) agreed to send me some pictures and video she had taken. I interviewed the property owner (Benjamin Phillips 858 688-6861) over the phone and he said he has owned the property for several years but does not know when the garage was built or if there was any grade changes. There is an inventory Fan Palm (QQ8205) located on the property and the customer is agreeable to removal so a meeting onsite will be arranged to discuss. | This outage was not preventable although the root flare was submerged in soil. The tree has been cleared from the conductor and out of the street. No further work is necessary. | 2020-03-20 14:20 | 2015-06-04
OUTAGE ID NUMBER: 150717E73913s | DISTRICT NAME: | 360 | 908 | 32451 VERNIE VISTA LN, VALLEY CENTER 92082 | Avocado | 2015-07-17 | JN1125 | P213348 P213347 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2015-07-01 | Y | 10.0 to 11.9 ft | Y | 2014-08-28 | N | 0.0 to 5.0 ft | Unable to Verify | 13.0 to 17.9 in | Other | 10.1 - 12 | No Record |  | None |  | No Record | No Record | N | This large Avocado (30-40ft – tall for a grove tree) appeared to be cut improperly (backcut only with no notch) by a contract grove worker and felled into the primary conductor bringing it down and damaging the Telco lashing. No one was hurt but a small spot fire (approx. 10ftX15ft) was extinguished by the responding fire agency. | The workers performing the stumping to the entire grove could not speak English. An interview of the property owners (Bobbie and Bob Sykes 760 638-3776) revealed the management company they contracted with to perform the work; Stehly Enterprises (owner Jerome Stehly 760 638-3443 office, 760731-6517 cell). Calls to the cell number indicate it has been disconnected and I have received no return call from the office number. | No further work is required here as all Avocados have been stumped. | 2020-03-20 14:20 | 2015-07-17
OUTAGE ID NUMBER: 150728E74847s | DISTRICT NAME: | 673 | 66 | 15925 VIA DEL ALBA, RANCHO SANTA FE 92067 | Eucalyptus | 2015-07-28 04:41 | CE2757 | P318541 P318540 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 318 - Tree contact as a result of growth/encroachment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 80.1 to 200 ft | 80.1 to 100.0 ft | 24.0 to 35.9 in | None | 80.1 - 100 |  |  | Root Rot |  | No Record | No Record | N | A large non inventory Eucalyptus uprooted and struck a stub pole (P199588) and guy splitting the pole and shaking the distribution pole (P318540) the guy was conected to causing phase to phase contact between poles P318540 - P318541. The tree had already been cleaned up but it appeared that the tree had little to no tap roots that would have stabalized the large tree in the very soft and sandy soil. |  | Our vegetation department will follow up with the county and the association to develop a plan to remove trees in the area to avoid future outages. | 2020-03-20 14:20 | 2015-07-28
OUTAGE ID NUMBER: 150805E75544s | DISTRICT NAME: | 520 | 255 | 707 F ST, CHULA VISTA 91910 | Palm-Fan | 2015-08-05 | PQ277 | P188040 P188041 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 318 - Tree contact as a result of growth/encroachment | City | Primary | 4.1 to 5.9 ft | Tree Failure | 2015-07-21 | N | 10.0 to 11.9 ft | N | 2014-09-30 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | Inventory Mex Fan Palm shed a seed pod during moderate winds. The seed pod crossed up on two phases of primary causing the outage. | N/A | Tree is in Chula Vista city ROW. area Forester negotiated the removal of 10 Mex Fans in the area as a preventative measure. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 150817E76388s | DISTRICT NAME: | 513 | 1435 | 3323 NUTMEG ST, SAN DIEGO 92104 | Palm-Feather | 2015-08-17 | QW821 | P733251 P2074173193 | 324 - Palm tree contact | 324 - Palm tree contact | City | Primary | 2.1 to 4.0 ft | Tree Growth | 2014-11-03 | Y | 10.0 to 11.9 ft | N | 2014-12-19 | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 8.0 to 12.9 in | None | 8.1 - 10 |  |  |  |  | No Record | No Record | N | Inventory Queen Palm QW821 had a frond lay across conductors in this span and caused primary outage. responding ETS cleared and reenergized. | Palms are on private property belonging to sensative customer Mr & Mrs Dougennis 619.280.7711. AF contacted regarding necessary removals. This was second outage at this location. | Removals and replacements were negotiated and agreed upon to prevent another outage here. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 150819E76543 | DISTRICT NAME: | 312 | 522 | 1210 S STAGE COACH LN, FALLBROOK 92028 | Palm-Fan | 2015-08-19 | GZ92 | P111147 P17019 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2015-05-29 | N |  | N |  | Y | 30.1 to 40 ft | 6.0 to 7.9 ft | 13.0 to 17.9 in | None | 8.1 - 10 | No Record |  |  |  | No Record | No Record | N | I reviewed this site and the information provided. I walked for several spans in either direction (4-way primary pole) and couldn’t find any Palms that could have caused an outage. There were Palms nearby but they weren’t tall enough to put any fronds on the lines especially since there wasn’t any weather events at the time of the outage. I called Station Y and got the number of the responding ETS, Louise Amivista 760 535-7907, and called him a few times. I left messages for him to call me back about this outage and have yet to hear from him. I feel there is no evidence to support a Palm-related outage here so my recommendation is to request a change in the outage cause code to bird-related 312 – Flashover/vegetation. That would be the only explanation as to why this was reported as tree-related. Mike Daleo wrote: I just called Louis and he answered his phone (go figure). I quizzed him for details and he stated emphatically that he did indeed remove palm material (frond or other, he wasn’t sure) from the line that caused the outage. With that, we have to assume his explanation and complete the investigation as such. Somehow the material made its way into lines even in the absence of known winds. | Nonoe | None | 2020-03-20 14:20 | 2015-08-20
OUTAGE ID NUMBER: 150823E76860 | DISTRICT NAME: | 376 | 354 | 30817 OLD HIGHWAY 395, ESCONDIDO 92026 | Pine | 2015-08-26 | FT3807 | P415300 P415301 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2015-06-15 | Y | 10.0 to 11.9 ft | Y | 2014-09-09 | N | 0.0 to 5.0 ft | Unable to Verify | 13.0 to 17.9 in | None | 0 - 2 | No Record |  | Dead Tree |  | No Record | No Record | Y | A dead Pine failed at the root base into the conductors bringing them down and causing a fire. The tree was listed for prune in the previous cycle but was not pruned and listed as no work required by the contractor (Davey Tree). The tree was identified as dead during the previous cycle but was not abated by the contractor so this outage was preventable. | None | The contractor was to complete an inquiry and report back to SDG&E Veg Mngt but no report has been received to date 1-11-16. | 2020-03-20 14:20 | 2016-01-11
OUTAGE ID NUMBER: 150828E77350s | DISTRICT NAME: | 518 | 42 | 2300 E 7TH ST, NATIONAL CITY 91950 | Palm-Fan | 2015-08-28 | EG2248 | P831862 P831896 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-08-06 | N | 10.0 to 11.9 ft | N | 2013-10-16 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 10.1 - 12 |  |  |  |  | No Record | No Record | N | A seed pod detached off an inventory Mex Fan Palm EG2248, layed across conductors, and caused the outage. Tree was identified for trim in upcoming trim cycle. | On site manager Stacy Grady described a explosion and saw a "fireball" on the pole. | Area Forester negotiated a removal of this palm to prevent another outage here. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 150915E78723s | DISTRICT NAME: | 520 | 1180 | 630 COCHRAN AVE, SAN DIEGO 92154 | Palm-Fan | 2015-09-15 | FY4208 | P187759 P187758 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2015-07-31 | N | 10.0 to 11.9 ft | N | 2014-10-17 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A seed pod and, or Palm frond detached off an inventory Mex Fan Plam in moderate wind and rain storm, layed on conductors, and caused the outege here. Tree had been flagged for upcoming routine tree trim of VMA 520. | Resident not home and did not repond to any door hanger request from AF to discuss palms. | No response from property owner. Trees were identified and trimmed with in upcoming routine tree trim schedule of VMA 520. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 150917E78985s | DISTRICT NAME: | 518 | 41 | 516 B AVE, NATIONAL CITY 91950 | Palm-Fan | 2015-09-17 | VL373 | P835456 P835465 | 324 - Palm tree contact | 324 - Palm tree contact | Private | Secondary | 0.0 to 2.0 ft | Tree Growth | 2015-08-12 | Y | 2.1 to 4.0 ft | Y | 2014-10-31 | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 13.0 to 17.9 in | None | 0 - 2 |  |  |  |  | No Record | No Record | N | An inventory Mex Fan Palm (VL373) located in National City ROW grew up through open wire secondary phases and most likely pushed one phase into butt guy. The resulting fault caused this palm and two others in contact with SSC (one and two spans away) to catch fire, causing transformer fire, outage, and Fire Department / Public Safety call out. | National City was contacted for necessary removal of this palm. | This palm and several other in the area under secodary wires were removed to prevent another outage here. Pre -inspection contractor, DRG, was notified to pursue removals of Fan Palms in ROWs under secondary lines. Current pre-inspection specifications do not pursue removals on open wire secondary. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 150930E79816s | DISTRICT NAME: | 520 | 255 | 707 F ST, CHULA VISTA 91910 | Palm-Fan | 2015-09-30 | FY2766 | P189566 P188041 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | City | Primary | 4.1 to 5.9 ft | Tree Failure | 2015-07-21 | N | 10.0 to 11.9 ft | N | 2014-09-30 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A seed pod detached off inventory Mex Fan Palm (FY2766), layed across conductors, picked up moisture from rain, cross phased, and caused the outage here. This tree, and others were identified for trim in upcoming routine tree trim cycle of VMA 520 | City of Chula Vista was contacted regarding removal of ten Fan Plams in the area. This was the second similar outage due to the line of plams in the ROW. | City of Chula Vista was contacted by AF and agreed to removing this and nine other palms in close proximity to high voltage powerlines. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151012E80606s | DISTRICT NAME: | 519 | 161 | 920 CARDIFF ST, SAN DIEGO 92114 | Palm-Fan | 2015-10-12 | GO2425 | P473359 P473360 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-08-13 | N | 10.0 to 11.9 ft | N | 2014-11-04 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A seed pod detached off an inventory Mex Fan Palm (GO2425), layed up on primary conductors, cross phasing, causing the outage here. This palm was identified in upcoming routine tree trim of VMA 519. | Commercial property mangement company, Cardiff Investments (Cinthia 619.465.02110) was contacted by AF offering removals and replacements. Property manager request 36" box replacements one for one and grind all stumps. | Trees were trimmed and will be pursued for removals with "reasonable" replacements offered. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151110E82588s | DISTRICT NAME: | 416 | 308 | 9249 RUFFIN RD, SANTEE 92071 | Italian Cypress | 2015-11-10 | ZZ19454 | P576105 P576104 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | City | Primary |  | Tree Failure |  | N |  | N |  | Y | 20.1 to 30.0 ft | 60.1 to 80.0 ft | 18.0 to 23.9 in | None | 60.1 - 80 |  |  |  |  | No Record | No Record | N | A non-inventory 60-75ft Italian Cypress toppled from base into wires located approximatly 75 ft away, impacting secondary underbuild, shook the priamry causing lines to slap together causing the outage. | Propert owner Dale Armstrong 619-520-7452 confirms whole tree failure and line slap caused the outage. | Whole tree failure unavoidable. Second Itaslian Cypress tree on property 75ft away from conductors was topped to safe height. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151115E82888s | DISTRICT NAME: | 210 | PL2 | 4604 NEWPORT AVE, SAN DIEGO 92107 | Palm-Fan | 2015-11-15 | FX20213 | P932321 P2109569444 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-10-16 | N | 10.0 to 11.9 ft | N | 2015-01-20 | Y | 50.1 to 60 ft | 6.0 to 7.9 ft | 8.0 to 12.9 in | None | 8.1 - 10 |  |  | Weak Branch Attachment |  | No Record | No Record | N | Palm fronds and seed pods sluffed off an inventory Mex Fan Palm (FX20213) in high winds and rain, cross phased on conductors, causing outage and wire down. This inventory palm was identified for trim in upcoming routine tree trim of VMA 210. | N/A tennant | Property mangement Company was contacted by Area Forester and removal authorization was secured. Palm has been removed. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151116E82897s | DISTRICT NAME: | 552 | 341 | 3556 LOMACITAS LN, BONITA 91902 | Eucalyptus | 2015-11-16 | OT1198 | P84596 P84595 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 2.1 to 4.0 ft | Tree Failure | 2015-08-28 | N | 10.0 to 11.9 ft | N | 2015-11-04 | Y | 60.1 to 80 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in | None | 10.1 - 12 |  |  | Weak Branch Attachment |  | No Record | No Record | N | Small twig off an inventory Eucalyptus detached in high winds, cross phased causing outage here. A lot of small Eucalyptus debris was found with in the span on AF investigation. | Responding ETS Rick Mendoza 619.719.8253 describes a very small Eucalyptus branch approximately 1/4" x 24" was pulled off conductors in stormy conditions. There is a transition from verticle to horizontal phases with in this span. | Euc OT1198 and AP6261 were trimmed for reliablity a few days prior to this outage. Sometimes new foliage is exposed to high winds after other foliage was cut away. tjhis appears to be the case. Trees sit on private property and property owner declined offer to remove theses trees | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151116E82958s | DISTRICT NAME: | 420 | 386 | 13530X E LOS COCHES RD, EL CAJON 92021 | Eucalyptus | 2015-11-16 | QV2176 | P878935 P677290 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 8.0 to 9.9 ft | Non-SDGE Crew Caused | 2015-11-11 | Y | 10.0 to 11.9 ft | N | 2015-02-05 | Y | 15.1 to 20.0 ft | 10.0 to 11.9 ft | 3.0 to 7.9 in | Other | 15.1 - 20 | No Record |  | None |  | No Record | No Record | N | Unqualified, third party tree work removal at adjacent property to 8580 Vista Del Verde LK did not go as planned. AF witnessed a cut Eucalyptus tree and two individuals with saw-zall pretending to not be reposible for cutting tree, AF confronts individuals and they reluctantly give names of Bill Bazemore 619.251.4222 and Anton Mityagin 619.414.4313. When asked if they cut the tree with the saw-zall they denied it. AF noticed saw cuts on tree trunk match the saw-zall seen in truck. Again these individuals deny they cut the tree. Tree located on adjacent property. | Unclear if these people are the owners of the property. | A tree crew was called out to remove remaining parts of tree that were hung up on conductors. Area Forester was able to convey the "near miss" safety aspects to the suspected tree workers. They seemed to understand this incident could have been a lot worse. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151118E83153s | DISTRICT NAME: | 464 | 445 | 1439 JEWEL VALLEY RD, BOULEVARD 91905 | Willow | 2015-11-18 | QJ4490 | P41897 P44952 | 704 - Line fault/tree trimming | 322 - Tree/branch/limb fell on the line or other electrical equipment | BLM | Primary | 20.0 to 30.0 ft | Non-Tree Related | 2009-07-07 | Y | 10.0 to 11.9 ft | N | 2008-08-27 | Y | 20.1 to 30.0 ft | 15.0 to 19.9 ft | 13.0 to 17.9 in | Other | 15.1 - 20 |  |  |  |  | No Record | No Record | N | 11-18-15 DSOR states tree contact cause code (322) for this outage. Area Forester investigation found no trees in span and recalls similar situation at this property 5-6 years ago where an excavator was used to clear the same pond of Willow trees and in that case the excavator made contact with high voltage wires causing an outage. same excavator was on scene and pond looks to be freshly cleared. | Property owner LeRoy Matter 9619-466-1384) was contacted for more information. He was not onsite the day of the outage. When asked for more information, Mr Matter said he would "look into it". Mt Empire OH supervisor confirms heavy equipment involved. With this confirmation, AF confronts property owner on incident. Mr Matter is then forth coming with more information. Mr Matter describes his ranch Foreman (Mike) was clearing Willows from pond and a portion of the willow being pulled out of pond made contact with the conductors and caused the outage with wire down. this is very similar to outage 5-6 years ago. | All Trees have been clered from this pond. A "near miss" safety converstion was had by Area Forester and property owner (Matter) regarding working safely around high voltage powerlines. cause Code should be changed to 704 -heavy equipment contact | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151128E83658s | DISTRICT NAME: | 477 | 1183 | 11669 VALLE VISTA RD, LAKESIDE 92040 | Eucalyptus | 2015-11-28 | PZ1977 | P470248 P470249 | 704 - Line fault/tree trimming | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Non-SDGE Crew Caused |  | Y |  | N |  | Y | 60.1 to 80 ft | 40.1 to 50.0 ft | 13.0 to 17.9 in | Other | 60.1 - 80 |  |  |  |  | No Record | No Record | N | Area forester investigation notices trees at the outage location have been cut and wood stacked on site. Leaves door hanger to speak to property owner. nearby property owner (no nmae given) states tree workers cut tree and tree fell into wires. | Area Forester interviews property owner. Property owner David Escobar 858-558-2599 explains he hired a tree company from a flyer on his front door and gave me the company name and contact information. Andy Anderson Tree Care (Any Anderson 619-212-0023). He assumed they were qualified. Mr Escobar did not witness the incident but was on site (in the house). He believes the tree may have brushed the conductors as tree was cut down. No injuries reported. | Area Forester offfers to asssit property owner in toppping the other dead dying trees on this property to safe height before hiring a tree company to remove the trees. | 2020-03-20 14:20 | 2015-12-23
OUTAGE ID NUMBER: 151213E84487 | DISTRICT NAME: | 605 | CD4 | 1542 OAK AVE, CARLSBAD 92008 | Pine | 2015-12-13 | SK95 | P124343 P21989 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2015-09-23 | N | 10.0 to 11.9 ft | N | 2009-07-13 | Y | 60.1 to 80 ft | Unable to Verify | 42.0 to 47.9 in | None | 30.1 - 40 | No Record |  | Root Rot |  | No Record | No Record | N | A large over-mature Torrey Pine failed at the roots during a rain event (El Nino) due in part to its size, location on a slope, irrigation pipes within 1ft of the base of tree, and a concrete pad installed at the base of the tree. This tree was located across the street from our lines. |  | No work required. | 2020-03-20 14:20 | 2015-12-14
OUTAGE ID NUMBER: 151226E85117 | DISTRICT NAME: | 305 | 451 |  | Italian Cypress | 2015-12-26 | CE2773 | P218563 P12058 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | Y |  | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in |  | 10.1 - 12 |  |  |  |  | No Record | No Record | N | A non-inventory Italian Cypress uprooted in high winds. The root system was comprimised due to it's proximity to the apartment complex. The tree was planted up against the building and didn't allow natural root growth on the back side of the tree which would have helped anchor it. Due to high winds the 50ft tree was unable support itself. The tree cuaght fire while laying on the conductors and a small 5x12ft fire started in the city easement below the wires. | No residents were available during investigation. | Seven more Italian Cypress trees on site will be trimmed to safe height to avoid future outages | 2020-03-20 14:20 | 2015-12-29
OUTAGE ID NUMBER: 151226E85118 | DISTRICT NAME: | 381 | 1235 | 3805 LA CANADA RD, FALLBROOK 92028 | Eucalyptus | 2015-12-26 | CD2 | P210302 P210303 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | Y |  | N |  | N | 50.1 to 60 ft | Unable to Verify | 13.0 to 17.9 in | None | 20.1 - 30 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | A leader within a tall, previously topped, Euc failed into the conductors and brought them down during a wind event. The tree was a non-inventory but should have been identified by PI and listed for Reliability pruning. | None | This tree was aurthorized by the property owner for removal. | 2020-03-20 14:20 | 2015-12-28
OUTAGE ID NUMBER: 160105E85484s | DISTRICT NAME: | 603 | 289 | 333 W D ST, ENCINITAS 92024 | Palm-Fan | 2016-01-05 | QQ4870 | P120266 P23363 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 15.0 to 19.9 ft | Tree Failure | 2015-10-26 | N | 10.0 to 11.9 ft | N | 2015-01-22 | Y | 40.1 to 50 ft | 20.0 to 30.0 ft | 13.0 to 17.9 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Palm seed pod detached during storm event and fell on primary and transformer jumper wire causing fuses to blow at P20805. |  | Removal of city palm is required. I will contact John Ugrob with city of Encinitas and secure removal. | 2020-03-20 14:20 | 2016-01-08
OUTAGE ID NUMBER: 160106E85572s | DISTRICT NAME: Metro | 518 | 130 | 3150 MAIN ST, SAN DIEGO 92113 | Eucalyptus | 2016-01-06 | EY3619 | P1899373383 P232685 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 322 - Tree/branch/limb fell on the line or other electrical equipment | Military | Primary | 8.0 to 9.9 ft | Tree Failure | 2015-08-07 | N | 10.0 to 11.9 ft | N | 2015-11-30 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 8.0 to 12.9 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Inventory Lemon Gum EY3619 had a lineside limb break off and hit conductors during "El Nino" storm conditions. Limb estimated to be 6" x 20+ft hit Military base housing parameter security fence as well causing causing slight damage. Tree was last trimmed on 11-30-15 at 10-12ft to side. | N/A | This tree (EY3619) no longer a threat. Adjacent tree has strom damage hanger and looks heavily weighted to lines. High priority memo was issued to make the second tree (EY3621) safe. | 2020-03-20 14:20 | 2016-01-14
OUTAGE ID NUMBER: 160106E85588 | DISTRICT NAME: | 606 | 130 | 2250 ALTA VISTA DR, VISTA 92084 | Palm-Fan | 2016-01-06 | GT2757 | P15326 P15325 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 50.1 to 60 ft | Unable to Verify | 13.0 to 17.9 in | None | 60.1 - 80 | No Record |  |  |  | No Record | No Record | N | On 1-12-16 Don Akau sent an email: I visited this location 2250 Alta Vista Drive and found fronds at the base of pole 15326 and along the overhead near property 2250. It appears we had a non-inventory fan Palm estimated 65 feet tall and 70 plus feet from the overhead lines on the west side which makes sense, direction of high wind and rains. The frond most likely snagged the primary and came into contact with the open wire secondary strung below. See attached pictures. However I found no evidence of palm fronds on the ground with burn makes. Further down the line to pole 118655 we have another fan palm (HM334) flagged for pruning but no evidence of any fronds detached near this palm or on this property. HM334 is also on the east side of the lines which would not be a likely cause during the winds pushing to the east. I would ask DRG to add this palm and have it added to the Davey WO in VMA 606. | None | Tree will be pruned on a memo. | 2020-03-20 14:20 | 2016-01-12
OUTAGE ID NUMBER: 160106E85601s | DISTRICT NAME: Metro | 527 | 158 | 1345 ELDER AVE, IMPERIAL BEACH 91932 | Eucalyptus | 2016-01-06 16:38 | FX16524 | P83836 P83837 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-07-14 | N | 10.0 to 11.9 ft | N | 2015-09-10 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 18.0 to 23.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | Inventory Euc (FX16524) had a backside limb detach and fall onto phone cable service wires. The impact shook facilities causing primary outage. This occurred during "El Nino" storm conditions. | 1-11-16 interview of on site tennant. He confirms the limb hit phone cables and heard pop of fuses nearby. | Property management company, Otay Reality, was contacted and removal of this Euc was authorized. Removal was forwarded to tree trim contractor. | 2020-03-20 14:20 | 2016-01-14
OUTAGE ID NUMBER: 160107E85634s | DISTRICT NAME: Metro | 469 | 442 | 7614 PINE BLVD, PINE VALLEY 91962 | Pine | 2016-01-07 04:19 | AN147 | P173194 P378690 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-06-30 | N | 10.0 to 11.9 ft | N | 2011-09-15 | Y | 20.1 to 30.0 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  | Dead Tree |  | No Record | No Record | Y | Dead inventory Pine (AN147) top snapped off during wind and snow "El Nino storm. the top of tree impacted primary facilities causing the outage. Pine was ID'd as DDRP on 6-30-15. Tree was in tree trim contractor's hand to be worked. However, this VMA (469) has been delayed due to environmental reviews and USFS protocols. |  | Stream line environmental reviews. | 2020-03-20 14:20 | 2016-01-14
OUTAGE ID NUMBER: 160107E85640s | DISTRICT NAME: Metro | 212 | 545 |  | Palm-Fan | 2016-01-07 06:38 | ZZ19456 | P933664 P2192569221 | 430 - Palm frond due to storm/high wind | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 80.1 to 100.0 ft | 13.0 to 17.9 in |  | 80.1 - 100 |  |  | Weak Branch Attachment |  | No Record | No Record | N | 40-50ft non-inventory Mex Fan Palm sloughed fronds and seed pods in "El Nino" storm conditions. The fronds were blown onto primary conductors 80ft away causing the outage on Cir 545. | Responding ETS, John Piraino 619.818.4417, states that he pulled fronds off primary conductors near P219288069221. | This 40-50ft tree 80ft away does not qualify for our tree inventory system. This was an isolated rouge palm frond in high winds. | 2020-03-20 14:20 | 2016-01-14
OUTAGE ID NUMBER: 160107E85648 | DISTRICT NAME: | 601 | 61 | 1050 STRATFORD CT, DEL MAR 92014 | Eucalyptus | 2016-01-07 08:06 | GD33 | P62032 P60534 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-03-03 | N | 10.0 to 11.9 ft | N | 2015-05-29 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 42.0 to 47.9 in |  | 15.1 - 20 |  |  | Root Rot |  | No Record | No Record | N | Inventory tree uprooted due to high winds and rain. The tree had signs of root rot. Pooling of rain water at the base along with high winds caused the tree to fail. The Euc was 40-50 ft tall and had no outward signs of root decay. It was side trimmed on 5/29/15 and should have been compliant. | A home contractor working on the house next door said that the heavy rain was streaming accross Stratford St and pooling at the base of the tree. He said he was standing next to the tree when another worker started to yell that the tree was falling. He ran to the south and observed the tree falling and striking the conductors. | Tree was cleaned up by private contractor and no follow up work is required. | 2020-03-20 14:20 | 2016-01-08
OUTAGE ID NUMBER: 160131E7302s | DISTRICT NAME: Eastern | 552 | 341 | 4202 LOMA PASEO, BONITA 91902 | Eucalyptus | 2016-01-31 15:20 | AP7620 | P204862 P185588 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-09-08 | N | 10.0 to 11.9 ft | N | 2013-11-01 | Y | 30.1 to 40 ft | 12.0 to 14.9 ft | 18.0 to 23.9 in |  | 15.1 - 20 |  |  | Root Rot |  | No Record | No Record | N | Large inventory Euc AP7620 failed at base in storm event damaging two poles, causing primary wire down, and is the cause of outage on Cir 341. | N/A | Whole tree failure requires no follow up. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160131E87227 | DISTRICT NAME: | 606 | MV1 | 1324 CYPRESS DR, VISTA 92084 | Palm-Fan | 2016-01-31 | GG3479 | P15600 P15805 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2016-01-13 | N | 10.0 to 11.9 ft | N | 2015-04-08 | N | 80.1 to 200 ft | Unable to Verify | 13.0 to 17.9 in | None | 6.1 - 8 | No Record |  | Dead Branch |  | Weak Branch Attachment | No Record | N | A tall Fan Palm had fronds release during a high wind storm event and land on the conductor and likely slide up the lines to pole P15805 and cause an outage. | Spoke to customer (Wendis Aposhian 760212-0194) and told her about what caused the outage. She was open to removing 4 Fan Palms (GG3479, UF1303, ST3541, and a non-inventory Fan at P15600) but needed to speak to her husband. Customer was to call me back by 2-16-16 but never did. | DRG Area Lead being asked to pursue a removal project at this site to help prevent further outages if possible. If not able to get all 4 trees mentioned in Resident Comments then will notify AF for Fatal Prune of GG3479, UF1303, and possibly ST3541. | 2020-03-20 14:20 | 2016-02-11
OUTAGE ID NUMBER: 160131E87232 | DISTRICT NAME: Northeast | 398 | 231 | 4694 SLEEPING INDIAN RD, FALLBROOK 92028 | Pine | 2016-01-31 | ON688 | P416245 P416244 | 420 - Tree contact due to storm/high wind | 420 - Tree contact due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-03-02 | Y | 10.0 to 11.9 ft | N | 2015-05-28 | N | 0.0 to 5.0 ft | Unable to Verify | 36.0 to 41.9 in | None | 15.1 - 20 | No Record |  | Co-dominant Branch |  | Included Bark | No Record | N | A large codominant leader with included bark broke out during a strong wind event and brought the lines down. Outage was preventable as this defect should have been mitigated years before. PI had full access to the property through a gate code within the tree records. | Customer filed a claim with SDG&E to clean up the tree leader that fell during the storm and repair the property (fence). That claim was denied. | A Same Day Memo was called 2-10-16 to top the remaining line-side leader below lines. PI was here 2-2-16 but did not access the property to properly inspect the tree. If they had they would have seen the remaining reliability work that needed to be done post the storm breakout. | 2020-03-20 14:20 | 2016-02-10
OUTAGE ID NUMBER: 160131E87232 | DISTRICT NAME: Northeast | 398 | 231 | 4694 SLEEPING INDIAN RD, FALLBROOK 92028 | Pine | 2016-01-31 | ON688 | P416245 P416244 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-03-02 | Y | 10.0 to 11.9 ft | N | 2015-05-28 | N | 0.0 to 5.0 ft | Unable to Verify | 36.0 to 41.9 in | None | 15.1 - 20 | No Record |  | Co-dominant Branch |  | Included Bark | No Record | N | A large codominant leader with included bark broke out during a strong wind event and brought the lines down. Outage was preventable as this defect should have been mitigated years before. PI had full access to the property through a gate code within the tree records. | Customer filed a claim with SDG&E to clean up the tree leader that fell during the storm and repair the property (fence). That claim was denied. | A Same Day Memo was called 2-10-16 to top the remaining line-side leader below lines. PI was here 2-2-16 but did not access the property to properly inspect the tree. If they had they would have seen the remaining reliability work that needed to be done post the storm breakout. | 2020-03-20 14:20 | 2016-02-10
OUTAGE ID NUMBER: 160131E87236 | DISTRICT NAME: Northeast | 611 | EOS2 | 1425 LA SALINA ST, OCEANSIDE 92054 | Eucalyptus | 2016-01-31 | FX4952 | P127114 P127115 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-08-12 | N | 10.0 to 11.9 ft | N | 2015-12-15 | N | 60.1 to 80 ft | Unable to Verify | 24.0 to 35.9 in | None | 12.1 - 15 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | A limb broke out during a high wind storm event and burned pretty good on the lines before causing the outage. The lines were not brought down. | Customer Jerry Collins (760 729-3116) heard a loud bang and saw limbs on the lines burning. | Tree is being GR pruned this month. Had Area Lead follow-up on removing line-side leaders. | 2020-03-20 14:20 | 2016-02-01
OUTAGE ID NUMBER: 160131E87238 | DISTRICT NAME: Northeast | 616 | 233 | 30626 N RIVER RD, BONSALL 92003 | Eucalyptus | 2016-01-31 | CD13 | P812601 P10101 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 30.1 to 40 ft | Unable to Verify | 36.0 to 41.9 in | None | 20.1 - 30 | No Record |  | Root Rot |  | No Record | No Record | N | This very large non-inventory Euc located across the street from our lines failed at the roots and broke P812601 during a high wind storm event. The tree had root rot probably from soil being placed on top of the root zone from road construction / maintenance years before as the base of the tree had several inches of accumulated soil around it and was partially buried above the basal flare. | No property owners present. | No further work required. | 2020-03-20 14:20 | 2016-02-01
OUTAGE ID NUMBER: 160131E87246s | DISTRICT NAME: | 416 | 3.9039e+32 | 10445 MAST BLVD, SANTEE 92071 | Eucalyptus | 2016-01-31 15:30 | ZZ19461 | Z871471 Z194415 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Other SDGE Facility |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 80.1 to 100.0 ft | 18.0 to 23.9 in |  | 80.1 - 100 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A relatively small branch estimated to be 1/2 - 1" x 24-36" detached off large Lemon Gum Euc, floated in high winds into Santee substation and landed on rack system of sub causing multiple circuit outage in substation in El Nino storm. | N/A | The trees around substation check out OK. Offending tree is on private property and looks to be professionally maintained. No follow up required. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160131E87250 | DISTRICT NAME: | 653 | 1001 | 17461 AVENIDA DE ACACIAS, RANCHO SANTA FE 92067 | Pine | 2016-01-31 | QS2602 | P112796 P112797 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-12-22 | N | 10.0 to 11.9 ft | N | 2015-03-05 | Y | 60.1 to 80 ft | 8.0 to 9.9 ft | 18.0 to 23.9 in |  | 12.1 - 15 |  |  | None |  | No Record | No Record | N | A large inventory pine uprooted in the rain and high winds. There were no signs of decay or root rot in the tree. Most likely caused by the heavy uptake of water from recent storms adding weight to the canopy and shrinking root system due to the extended drought. The high winds during the last storm tipped the balance and caused the uproot. |  | This tree is no longer a danger to the lines. I did leave a message for the customer asking if they were interested in removing any of the other pines in that span. | 2020-03-20 14:20 | 2016-02-04
OUTAGE ID NUMBER: 160131E87256 | DISTRICT NAME: | 311 | 475 | 14411 NORWALK LN, POWAY 92064 | Cypress | 2016-01-31 | CE2786 | P512991 P512992 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 424 - Deenergized for safety-tree trimming | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in |  | 12.1 - 15 |  |  |  |  | No Record | No Record | N | A large Cedar tree uprooted and fell across the primary causing the outage. No signs of root rot or decay. Most likely caused by the heavy uptake of water during recent storms and a shrinking root system from the extended drought. The winds during the last storm tipped the balance and caused the uproot |  | The tree uprooted and is no longer a danger to the lines. No follow up required | 2020-03-20 14:20 | 2016-02-04
OUTAGE ID NUMBER: 160131E87257 | DISTRICT NAME: | 310 | 476 | 12922 CAMINO DEL VALLE, POWAY 92064 | Eucalyptus | 2016-01-31 | EI1770 | P513894 P513893 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2015-04-23 | N | 10.0 to 11.9 ft | N | 2012-07-03 | Y | 80.1 to 200 ft | 15.0 to 19.9 ft | 36.0 to 41.9 in |  | 20.1 - 30 |  |  | Root Rot |  | No Record | No Record | N | A large inventory Euc uprooted and fell across the Primary. There were signs of root rot and decay. The heavy rain and wind during the recent storm caused the tree to fail due to a comprimised root system. | Customer said there were no fungal growths at the base that would indicate root rot | This tree is no longer a threat to the wires. There are two other inventory trees that the customer is going to have removed so there is no longer any tree issues at this address. | 2020-03-20 14:20 | 2016-02-10
OUTAGE ID NUMBER: 160131E87258 | DISTRICT NAME: | 362 | 450 | 3044 KAYWOOD DR, ESCONDIDO 92026 | Eucalyptus | 2016-01-31 | CE2792 | P213054 P816036 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | Y |  | N |  | Y | 50.1 to 60 ft | 20.0 to 30.0 ft | 42.0 to 47.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Large Euc branch broke out of non-inventory tree. Clear signs of included bark and weak attachments. Due to strong winds and rain the branch broke out at the inclusion. several other weak attachments from previous topping broke out and would have struck the line if the other included branch had not taken them down first. |  | No other work is required to the tree at this time. A follow up with DRG to find out why this tree wasn't identified as a hazard. | 2020-03-20 14:20 | 2016-02-09
OUTAGE ID NUMBER: 160131E87290 | DISTRICT NAME: | 616 | 486 | 427 VANDEGRIFT BLVD, OCEANSIDE 92057 | Brisbane Box | 2016-01-31 | CD14 | Z31079 Z317860 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 40.1 to 50 ft | Unable to Verify | 13.0 to 17.9 in | None | 20.1 - 30 | No Record |  | Root Rot |  | Girdled Roots | No Record | N | A medium-sized non-inventory Brisbane Box tree failed at the root plate during a high wind storm event and fell into the primary and possibly contacted the 69kV as well. The tree had a very limited root zone with heavy irrigation and was located up on top of an embankment next to an apartment building. | No property owners present. | Property managers had remaining tree stump removed and allowed removal of all Brisbane Box trees near the conductors. | 2020-03-20 14:20 | 2016-02-01
OUTAGE ID NUMBER: 160131E87297 | DISTRICT NAME: | 602 | DM1 | 752 E SOLANA CIR, SOLANA BEACH 92075 | Eucalyptus | 2016-01-31 | TO553 | P27063 P27062 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2015-05-27 | Y | 10.0 to 11.9 ft | N | 2015-07-31 | Y | 60.1 to 80 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 15.1 - 20 |  |  | Co-dominant Branch |  | No Record | No Record | N | Two large Euc branches grew together comprimising the integrity of both branches. Due to the rain and high winds one of the branches split from the other striking the primary and taking out three spans of wire, the top of one pole and cross arms on another. |  | Any further danger from the remaining branch was taken care of by a tree crew during the outage. A follow up with DRG will be done to see why this defect wasn't caught in recent years | 2020-03-20 14:20 | 2016-02-15
OUTAGE ID NUMBER: 160131E87298 | DISTRICT NAME: | 707 | 796 | 30122 NIGUEL RD, LAGUNA NIGUEL 92677 | Eucalyptus | 2016-01-31 | FC3682 | P220937 P220936 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2015-07-20 | Y | 8.0 to 9.9 ft | N | 2015-12-18 | N | 50.1 to 60 ft | Unable to Verify | 13.0 to 17.9 in | None | 10.1 - 12 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | This tall, poorly-tapered Euc had a large canopy leader fail during a high wind storm event. Tree burned line but didn’t bring them down. Tree was listed only for prune 7-20-15 but tree ID’s FC3677 and FC3683 located on either side of this tree were listed for GR prune (?). This tree should have been listed for GR prune. | No property owners present. | Tree is being GR pruned. All the trees along this road were listed XT due to the City of Laguna Niguel delaying the encroachment permitting until mid-Feb 2016. Otherwise these trees would have at least been pruned by 10-31-15 and that could have possibly prevented this outage. | 2020-03-20 14:20 | 2016-02-09
OUTAGE ID NUMBER: 160131E87299 | DISTRICT NAME: | 313 | FB2 | 625 PALOMINO RD, FALLBROOK 92028 | Eucalyptus | 2016-01-31 | CD5 | P16969 P316687 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 50.1 to 60 ft | Unable to Verify | 24.0 to 35.9 in | None | 12.1 - 15 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | A medium sized non-inventory Euc had a leader fail into the conductors during a high wind storm event and brought down the neutral. The ETS de-energized the primary for safety and repairs. This tree has poorly-tapered leaders and an open field next to it allowing the canopy to be susceptible to high wind events. | I spoke to a grounds keeper supervisor and let him know we may pursue removals. He said fine and that they would be willing to discuss. | Tree needs to be topped to a safe height but during Routine. | 2020-03-20 14:20 | 2016-02-10
OUTAGE ID NUMBER: 160131E87304 | DISTRICT NAME: | 673 | 68 | 13650 CARMEL VALLEY RD, SAN DIEGO 92130 | Eucalyptus | 2016-01-31 | CE2790 | P814382 P814383 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | Y |  | N |  | Y | 50.1 to 60 ft | 20.0 to 30.0 ft | 24.0 to 35.9 in |  | 30.1 - 40 |  |  | Co-dominant Branch |  | No Record | No Record | N | A large 4 trunk Euc had one of the leads breakout due to a heavy inclusion at the base. Uptake of water has been minimal due to the drought, so recent rains and heavy uptake of water by the tree made the canopy heavy and could no longer support the inclusion |  | This tree no longer poses a threat to the primary. Even though this tree is outside of normal parameters for PI it should have been caught by DRG. I will follow up on this and have them inspect the other two spans north of this outage. | 2020-03-20 14:20 | 2016-02-09
OUTAGE ID NUMBER: 160131E87310s | DISTRICT NAME: Eastern | 406 | 949 | 5636 NOKOMIS ST, LA MESA 91942 | Eucalyptus | 2016-01-31 15:02 | TL196 | P275219 P275221 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2016-01-20 | N | 10.0 to 11.9 ft | N | 2015-04-15 | Y | 30.1 to 40 ft | 8.0 to 9.9 ft | 8.0 to 12.9 in | None | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A small backside limb detached and fell onto primary wires during storm conditions causing outage on Cir 949 | N?/A | inventory tree is managed in VMS. no work required at this time. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160131E87328 | DISTRICT NAME: | 614 | 1081 | 1858 TENNIS PL, ENCINITAS 92024 | Eucalyptus | 2016-01-31 | CE2791 | P229536 P229537 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 50.1 to 60.0 ft | 18.0 to 23.9 in |  | 60.1 - 80 |  |  |  |  | No Record | No Record | N | A large non-inventory Euc uprooted and fell across the primary. No signs of root rot or decay. The tree is on a slope. Heavy uptake of water, weakened soil, and the slope all had a factor in the uproot. This outage was not avoidable. |  | This tree is no longer an issue, however several other trees on the slope were given to DRG to add and issue for reliability work | 2020-03-20 14:20 | 2016-02-09
OUTAGE ID NUMBER: 160131E87329 | DISTRICT NAME: | 302 | 188 | 1144 HIGHLAND HEIGHTS LN, ESCONDIDO 92026 | Pine | 2016-01-31 | OS2525 | P212911 P212910 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private |  | 4.1 to 5.9 ft | Tree Failure | 2015-05-07 | N | 10.0 to 11.9 ft | N | 2015-09-01 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 8.0 to 12.9 in |  | 20.1 - 30 |  |  | None |  | No Record | No Record | N | A large healthy Pine uprooted and fell across the primary taking out two phases of primary. There was no sign of root decay or rot. There were several very large boulders in the root zone that may have kept the soil from compacting and holding the roots securely. The uproot was unpreventable and was caused by the rain and strong winds |  | The tree uprooted completely and is no longer a threat to the wires. | 2020-03-20 14:20 | 2016-02-11
OUTAGE ID NUMBER: 160131E87336 | DISTRICT NAME: | 364 | 239 | 4800X DULIN RD, FALLBROOK 92028 | Eucalyptus | 2016-01-31 | CD6 | P714281 P169304 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 40.1 to 50 ft | Unable to Verify | 13.0 to 17.9 in | None | 20.1 - 30 | No Record |  | Root Rot |  | No Record | No Record | N | A medium sized non-inventory Euc located on an embankment failed at the roots and landed on the primary during a high wind storm event and burned there before the cross arm broke. The roots showed signs of rot likely due to drought. ETS de-energized primary for safety. This could have been a significant fire because of the tree sitting on the wire and the limbs burning but there was no fire on the ground to report. | None. | DRG Area Lead being asked to pursue a GR project at this site to help prevent further outages if possible. | 2020-03-20 14:20 | 2016-02-10
OUTAGE ID NUMBER: 160131E87337s | DISTRICT NAME: Eastern | 456 | 93 | 4853 EDGEVIEW DR, EL CAJON 92020 | Eucalyptus | 2016-01-31 22:34 | JD245 | Z371368 Z371367 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-10-22 | N | 10.0 to 11.9 ft | N | 2015-01-28 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 60.0 to 80.0 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Inventory Euc JD245 toppled in high winds and rain, caught 69kv primary underbuild causing primary outage on Cir 93. No known effect to 69kv. | N/A | Whole tree failure requires no follow up. Other trees on property are managed by VMS. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160131E87358 | DISTRICT NAME: | 616 | 231 | 1515 SLEEPING INDIAN RD, OCEANSIDE 92057 | Eucalyptus | 2016-01-31 | QQ7926 | P819941 P619940 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 15.0 to 19.9 ft | Tree Failure | 2015-08-31 | N | 15.0 to 19.9 ft | N | 2013-01-11 | N | 50.1 to 60 ft | Unable to Verify | 24.0 to 35.9 in | None | 20.1 - 30 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | This tree, located amongst a group of other tall, skinny Eucs, likely had a limb break out and blow into the conductors during a high wind storm event. The trees are located across the street from the conductors but evidence of large limbs from these trees were located under the facilities after this storm event. | Neighbor was home (formerly Force Pruned customer) and he gave me the homeowner’s personal contact number of Tisha Bulloch 760 724-1079 hm and 760 805-0849 cell. | DRG Area Lead being asked to pursue a GR or Removal project at this property to help prevent further outages if possible. | 2020-03-20 14:20 | 2016-02-22
OUTAGE ID NUMBER: 160201E87375s | DISTRICT NAME: | 212 | 545 |  | Palm-Fan | 2016-02-01 00:26 | ZZ19462 | P933680 P933680 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 100.1 ft + | 13.0 to 17.9 in |  | 100.1 - '+' |  |  | Weak Branch Attachment |  | No Record | No Record | N | A loose frond detached in storm conditions and may have "scooted" along the roof of 3 story apartment building, then blown by winds off roof and onto primary conductors causing outage on Cir 545. Mex Fan Plams are lined in front of the buildings along Ocean Front Walk. Conductors are in alley 100ft away. | N/A | This seems to be isolated event requirees no follow up. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160203E87695 | DISTRICT NAME: | 606 | BN1 | 1345 TOWER DR, VISTA 92083 | Eucalyptus | 2016-02-03 | CD11 | P166364 P18285 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary |  | Non-SDGE Crew Caused |  | Y |  | N |  | N | 0.0 to 5.0 ft | Unable to Verify | 18.0 to 23.9 in | Other | 20.1 - 30 | No Record |  | None |  | No Record | No Record | N | A large non-inventory Euc tree was being removed by a third-party contractor (Cesar Palacios - Master Tree Services - 760 917-7470). While he was within the tree canopy, cutting branches, a large leader he cut fell into the conductors. He says he was not injured. No fire was reported or evidence witnessed. The tree was cleaned up when I got there. | I spoke to Cesar and while very apologetic, admitted he made a big mistake cutting branches that large, next to the conductors, without knowing for sure if they would clear them. We had somewhat of an emotional conversation as he became aware of what could have happened to him had he been shocked or electrocuted. He assured me he would contact SDG&E in the future if he plans to remove trees near our conductors. The property info is: Justine Lounibos (account was still listed to her father Edward Lounibos but he has been deceased for some time she said) 1345 Tower Dr. Vista, CA 760 420-8589 cell | None | 2020-03-20 14:20 | 2016-02-17
OUTAGE ID NUMBER: 160205E87894 | DISTRICT NAME: | 311 | 927 | 13535 APACHE RD, POWAY 92064 | Eucalyptus | 2016-02-05 | RK2959 | P311541 P311542 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-03-24 | N | 10.0 to 11.9 ft | N | 2015-07-28 | Y | 40.1 to 50 ft | 8.0 to 9.9 ft | 48.0 to 53.9 in |  | 20.1 - 30 |  |  | None |  | No Record | No Record | N | A large inventory Euc uprorooted and fell on the primary. No root rot or decay present. The customer said there was heavy pooling of water at the base that lasted for several days after the recent storm. The Euc probably had a slight lean towards the wires and toppled when the canopy got heavy from the uptake of water and finaly fell over. | Customer said water pools under the tree during rains. | This tree is no longer a threat to the wires. No follow up required. | 2020-03-20 14:20 | 2016-02-06
OUTAGE ID NUMBER: 160209E88126 | DISTRICT NAME: | 352 | 470 | 14600 SAN PASQUAL VLY RD, ESCONDIDO 92027 | Avocado | 2016-02-09 | RZ1122 | P618405 P618406 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-06-26 | N | 10.0 to 11.9 ft | N | 2015-08-12 | Y | 30.1 to 40 ft | 4.1 to 5.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  |  |  | No Record | No Record | N | An Avacado branch heavy with fruit broke out and fell across the lines causing the fuse to blow. |  | Will have DRG inspect and issue work on Avocados heavy with fruit that could cause an outage. | 2020-03-20 14:20 | 2016-02-16
OUTAGE ID NUMBER: 160210E88129 | DISTRICT NAME: | 653 | 288 | 17653X LOS MORROS, RANCHO SANTA FE 92067 | Eucalyptus | 2016-02-10 | CE2793 | P15874 P15873 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 20.0 to 30.0 ft | 13.0 to 17.9 in |  | 30.1 - 40 |  |  | Co-dominant Branch |  | No Record | No Record | N | A large non-inventory Euc had a branch breakout that fell across the wire and caused the outage. The branch was still hung up in the tree so it was hard to tell if it was included bark. The heavy uptake of water from recent rain events and weaked branches due to the drought is causing branches to get tip heavy and breakout. |  | This tree still requires work and has been issued as a next day memo along with another non-inventory and inventory tree for reliability work to abate any potential for future breakouts. | 2020-03-20 14:20 | 2016-02-15
OUTAGE ID NUMBER: 160214E88483 | DISTRICT NAME: | 398 | 231 | 550 GEORGINE RD, FALLBROOK 92028 | Eucalyptus | 2016-02-14 | CD12 | P414190 P414191 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary |  | Non-SDGE Crew Caused |  | Y |  | N |  | N | 40.1 to 50 ft | Unable to Verify | 13.0 to 17.9 in | Other | 20.1 - 30 | No Record |  | None |  | No Record | No Record | N | A third-party neighbor (former firefighter) cut a medium-sized non-inventory Euc, located across the street from our lines, at the base with a poor notch and backcut. The tree didn’t fall parallel with the street as planned because there was no rope (reported by the property owner) to guide the direction of fall. So it struck our lines instead. No one was hurt and there was no fire. | Spoke to Mr Zucker about incident. I’m waiting on the contact info for this individual from the property owners so I can discuss powerline safety with him. The property owners have no plans to cut anymore trees on the property. | None. | 2020-03-20 14:20 | 2016-02-17
OUTAGE ID NUMBER: 160307E90170 | DISTRICT NAME: | 363 | 599 | 236 DEER SPRINGS RD, SAN MARCOS 92069 | Eucalyptus | 2016-03-07 | SM5017 | P116474 P216795 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2016-01-25 | N | 10.0 to 11.9 ft | N | 2013-03-28 | Y | 40.1 to 50 ft | Unable to Verify | 8.0 to 12.9 in | None | 10.1 - 12 | No Record |  | None |  | No Record | No Record | N | A co-dominant top of a medium sized Euc broke out in a storm event and brought down the lines and broke the pole at P216795. Tree was already listed PIP and Davey Tree already had this VMA Routine Work Package to start by 3-1-16 but had not gotten to this location yet. | The property manager was there and spoke to me about what happened. | We are removing this and 3 other Eucs nest to it to prevent any further issues. | 2020-03-20 14:20 | 2016-03-08
OUTAGE ID NUMBER: 160307E90183s | DISTRICT NAME: | 450 | 246 | 9485X CHIMNEY ROCK LN, EL CAJON 92021 | Sycamore | 2016-03-07 11:54 | EX1505 | P75105 P75540 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2015-12-04 | N | 15.0 to 19.9 ft | N | 2016-02-26 | Y | 15.1 to 20.0 ft | 15.0 to 19.9 ft | 42.0 to 47.9 in |  | 20.1 - 30 |  |  | Mechanical |  | No Record | No Record | N | An inventory Sycamore (EX1515) rooted on a bank of a streambed had it's root zone eroded by high water (El Nino storms). The whole tree fell toward conductors and caught the primary wires causing outage on Cir 246. The tree was recently ID'd and trimmed as Green Reliability tree on 2-26-16. The tree failed due to root zone erosion and high winds on 3-7-16. | N/A | Whole tree failure does not require follow up tree trim. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160307E90202s | DISTRICT NAME: | 400 | 401 | 7108 BOBHIRD DR, SAN DIEGO 92119 | Palm-Fan | 2016-03-07 14:33 | SQ3002 | P677710 P677711 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 8.0 to 9.9 ft |  | 2016-01-22 | N | 10.0 to 11.9 ft | N | 2015-04-10 | Y | 50.1 to 60 ft | 8.0 to 9.9 ft | 8.0 to 12.9 in |  | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | a frond shed off an ionventory Mex Fan POalm SQ3002 during a rain and wind event. The frond was believed to have cross phased. This palm along with two other on this property was identified for trim on 1-22-16 for the annual VMA 400 routine trim cycle scheduled for April 2016. | N/A | Tree has shed its fronds in storm. This one and two other are scheduled for annual tree trim of VMA 400 scheduled 4-16. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160307E90243s | DISTRICT NAME: Eastern | 406 | 88 | 6945 OREGON AVE, LA MESA 91942 | Eucalyptus | 2016-03-07 21:18 | FR4719 | P277141 P474951 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-01-21 | N | 10.0 to 11.9 ft | N | 2014-07-25 | Y | 60.1 to 80 ft | 6.0 to 7.9 ft | 24.0 to 35.9 in |  | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb from an inventory Euc (FR4719) detached in wind and rain, fell onto conductors between P277141 and P474951 causing wire down across Lake Murry Blvd at P277140. This was a multi day outage event. This tree was ID'd as Green Reliability on 1-21-16. It was in the routine VMA 406 work package assigned to tree trim contractor at outage date 3-8-16. | N/A | Area Forester followed up and obtained removal agreement with property owner. Tree was removed the following days after outage. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 16030E90178s | DISTRICT NAME: | 416 | 392 | 8355 GRAVES AVE, SANTEE 92020 | Pine | 2016-03-07 11:42 | ZZ19463 | P477974 P477975 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  |  |  | N |  | N |  | Y | 60.1 to 80 ft | 30.1 to 40.0 ft | 18.0 to 23.9 in |  | 40.1 - 50 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A relatively small piece of brush / "flyer" from a non-inventory Canary Island Pine tree detached in wind and rain, laid on conductors, causing the outage on Cir392. | Responding ETS confirms small piece of Pine brush found on primary conductors, was cleared and then re-energized. | The non-inventory Pine checks out OK. This seems to be an isolated case and requires no follow up tree trim. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160315E90913s | DISTRICT NAME: | 405 | 733 | 4301 DATE AVE, LA MESA 91941 | Eucalyptus | 2016-03-15 10:34 | FI3913 | P376331 P376331 | 626 - SDG&E Contractor line fault/tree trimming | 626 - SDG&E Contractor line fault/tree trimming | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2015-11-25 | Y | 12.0 to 14.9 ft | N | 2015-03-12 | Y | 60.1 to 80 ft | 8.0 to 9.9 ft | 48.0 to 53.9 in | Contractor | 8.1 - 10 | Asplundh Tree Experts |  |  |  | No Record | No Record | N | While working assigned Green Reliability (GR) trim on an inventory Euc FI3913, a relatively small log was cut and thrown clear of conducotrs. The log made impact to corner down guy on P376311 causing solid copper wire to pull from old sleeve repair causing wire to come down and the outage on Cir 733. No injuries, no fires, no damage reported. | N/A | Contractor Safety Standown was scheduled and commenced to all UTS tree contract personel with focus on targets below trees assigned trim and identifying old hardware that may need repair. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160405E92446 | DISTRICT NAME: | 654 | 859 | 1535 LONE OAK RD, VISTA 92084 | Eucalyptus | 2016-04-05 | QJ802 | P111094 P111093 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 10.0 to 11.9 ft | Non-SDGE Crew Caused | 2016-01-19 | Y | 10.0 to 11.9 ft | Y | 2015-03-19 | N | 30.1 to 40 ft | Unable to Verify | 60.0 to 80.0 in | Other | 10.1 - 12 | No Record |  | No Record |  | No Record | No Record | N | A medium sized Euc was being removed (along with another FN14433) by a private contractor (Green Horizons Landscape and Maintenance which is also the property owners) when they cut and felled a leader improperly toward the overhead primary, bringing the line down. A small fire had started at the base of P111093 approximately 6ftX4ft but was quickly extinguished by the crew. No injuries occurred. | In my phone conversation with the Tree Manager Hugo Curiel (760 801-6588) he said the crew was rushing and was aware the lines were close but shouldn’t have tried to fell the limb toward the lines. He said they do not have a line-clearance training program but discuss jobsite safety and powerlines before the jobs start typically. I told him we would have removed the trees free of charge and he was unaware of that and promised he would reach out to us in the future if their projects were close to our facilities. In my interview with the tenant at the property he said he heard a loud “boom” and saw a small puff of smoke by the pole but no fire. | The tree stumps were treated with a herbicide the next day by Davey and additional trees onsite are being pursued for removal. No additional work required on the two trees as they were already cut as low as possible due to steel objects within the base of the tree. | 2020-03-20 14:20 | 2016-04-06
OUTAGE ID NUMBER: 160407E92652 | DISTRICT NAME: | 552 | 341 | 3891 GREVILLA WY, BONITA 91902 | Eucalyptus | 2016-04-07 12:26 | FI216 | P85179 P85180 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2015-09-03 | N | 10.0 to 11.9 ft | N | 2015-11-09 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in |  | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb 4-6" x 12-16ft) shed off an inventory Euc FI216 impacted a service wire or down guys at P85719 and caused outage on Cir 341. Conditions were calm. Tree was recently privately trimmed all but the upper portion above the wires. This may have contruibuted to the outage due to heavy lineside growth that was not addresed with the rest of the tree. | N/A | A memo was issued to trim another limb on same tree in same condition as the one that failed. In addition, a second Euc tree (FI209) in the area was observed to have same weak attachments and a memo to clear a large dead limb on stub guy P250608 as follow up. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 160505E94960s | DISTRICT NAME: | 519 | 161 | 920 CARDIFF ST, SAN DIEGO 92114 | Palm-Fan | 2016-05-05 | FS5792 | P672892 P472707 | 326 - Palm frond contact | 326 - Palm frond contact | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-08-13 | N | 10.0 to 11.9 ft | N | 2015-12-10 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 10.1 - 12 |  |  |  |  | No Record | No Record | N | The husk portion of a Mexican Fan Palm detached and fell onto stand off pin on primary pole hardware causing the outage. | N/A | The husk portion(part of frond where it is attached to trunk, is usually cut here) normally is not big enough to cross phase powerlines. In this case, the husk made a "lucky hit" and hit where two phases are close together on the bank of transformers mounted on the pole. A request to remove was offered to the commercial property mangement company. | 2020-03-20 14:20 | 2016-06-24
OUTAGE ID NUMBER: 16051395784 | DISTRICT NAME: | 305 | 514 | 936 LUNA VISTA DR, ESCONDIDO 92025 | Oak | 2016-05-13 | AH7437 | P316182 P410237 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-02-24 | N |  | N |  | Y | 20.1 to 30.0 ft | 6.0 to 7.9 ft | 54.0 to 59.9 in | None | 30.1 - 40 |  |  | Heart Rot |  | No Record | No Record | Y | Very large, multi-trunk live oak (40 feet x 55" DBH) failed at junction of trunks at ground level. One trunk struck the underbuild SSC secondary line breaking the secondary crossarm, and brought down the service to two customers. The primary wire was not struck by the tree. The primary outage was forced to allow the SDG&E line crew to safely restore service. No fire or injuries occurred. The oak tree was live and inventory to Veg Mgmt. The tree (AH7437) was last inspected by VM on 2/24/16 and listed clear. It would have likely been difficult to determine at that time that the tree's failure was imminent as there may not have been any outward visual sign of interior rot. |  | Tree failed at ground level and poses no further threat to the facilities. | 2020-03-20 14:20 | 2016-05-16
OUTAGE ID NUMBER: 160513E95727 | DISTRICT NAME: | 408 | CG2 | 4947 VISTA ARROYO, LA MESA 91941 | Century Plant | 2016-05-13 | JH85 | P272605 P575754 | 318 - Tree contact as a result of growth/encroachment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Growth |  | N |  | N |  | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 3.0 to 7.9 in | None | 2.1 - 4 |  |  |  |  | No Record | No Record | N | Agave (Century plant) flower stalk grew into primary wire. Customer heard sparking as a result of the stalk's contact with the wire and called SDG&E. Line crew responded and opened fuses forcing the outage so the tree crew could safely cut the flower stalk in the clear. No fire or injuries resulted. |  | Veg Mgmt has been conducting an active inspection of all inventory century plants in the service territory for the past two weeks. This location had not yet been inspected during this patrol. | 2020-03-20 14:20 | 2016-05-16
OUTAGE ID NUMBER: 160528E96935 | DISTRICT NAME: | 366 | 214 | 20113 HIGHWAY 76, PAUMA VALLEY 92061 | Sycamore | 2016-05-28 | CD16 | P36160 P215848 | 312 - Flashover/vegetation | 312 - Flashover/vegetation | Private | Primary |  | Non-Tree Related |  | N |  | N |  | N | 30.1 to 40 ft | No Record | 8.0 to 12.9 in | No Record | 100.1 - '+' | No Record |  | None |  | No Record | No Record | N | A small dead branch was found on P36160 by the ETS and was likely carried there by a bird. There was a lot of small bird activity in the immediate area and a bird’s nest within the trunk of an adjacent inventory Sycamore (FQ4130). Weather conditions were mild but significant fog was present. | Customer (Livia Berg Johnson 760 742-4234) saw the branch with the ETS and described it as about 1ft long. Reported area was very foggy at the time. | Forester is pursuing removal of FQ4130 due to decay in trunk. Customer will watch tree for bird activity near cavity in trunk to see if there is an active nest. If not then will call me to sign removal card or wait until outside breeding season to have us remove. | 2020-03-20 14:20 | 2016-05-30
OUTAGE ID NUMBER: 16061E98127s | DISTRICT NAME: | 405 | 733 | 4604 ACACIA AVE, LA MESA 91941 | Palm-Fan | 2016-06-13 | QC747 | P70357 P70390 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 326 - Palm frond contact | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2015-11-20 | N | 12.0 to 14.9 ft | N | 2016-03-22 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A frond detached from a very tall 100ft+ inventory Mexican Fan Palm (QC747), fell onto primary conductors causing the outage. A dead frond with burn marks was found across the street from given DSOR location. | N/A | There are several very tall 100ft+ Mex Fan Plams within city of La Mesa RoW in this area. The palms are too tall for 70ft lift, must be bucket jumped. Several have defects in the trunks that make them a worker safety issue. Because of this the plalms were XT'd for routine tree trim and a removal request on 10-19-15 to the city went unanswered. La Mesa City tree trim contractor WCA have choosen not to trim for safety reasons also. A current request to city of La Mesa has been made for removal of these dangerous palms. | 2020-03-20 14:20 | 2016-06-24
OUTAGE ID NUMBER: 160620E98723 | DISTRICT NAME: Northeast | 388 | RB1 | 8215 RAINBOW HEIGHTS RD, FALLBROOK 92028 | Oak | 2016-06-20 | FH2491 | P119508 P119507 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | State | Secondary | 10.0 to 11.9 ft | Tree Failure | 2015-07-13 | N | 10.0 to 11.9 ft | N | 2012-10-15 | N | 40.1 to 50 ft | Unable to Verify | 24.0 to 35.9 in | None | 6.1 - 8 | No Record |  | Decayed Branch |  | No Record | No Record | N | A large limb from an inventory Oak (FH2491) failed into the SSC and caused the secondary leads to interfere with the safe restoration of secondary service so the primary line was de-energized for safety. The remains of the leader showed signs of decay on the top of the branch, as viewed from the ground. This outage was not preventable as the leader was on the backside of the tree and away from the primary conductors and was more of an CMP maintenance issue. | I spoke to a Calfire representative who was there when the incident occurred. He showed me the location and explained what he saw. They had their crews clean up the tree branch. He observed decay in the branch. He also stated there was no injuries or fire. To his knowledge Calfire was not called to the scene but responded as it was on the property of the Rainbow Conservation Camp where they have a large maintenance and training yard. | There was no further issue with the tree and the limb was already cleaned up. No further work required. | 2020-03-20 14:20 | 2016-06-24
OUTAGE ID NUMBER: 160627E99150 | DISTRICT NAME: | 381 | 230 | 1753 CARRIAGE LN, FALLBROOK 92028 | Oak | 2016-06-27 | AD5557 | P713207 P713208 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft |  | 2015-06-10 | N | 10.0 to 11.9 ft | N | 2014-09-03 | N | 0.0 to 5.0 ft | Unable to Verify | 0.0 to 2.9 in |  | 10.1 - 12 |  |  | Root Rot |  | No Record | No Record | N | A medium sized Oak, located on a steep embankment in soft, dry soils, failed at the roots bringing down a primary wire. No report of injuries or fire. It was a hot and dry day and the loose and desiccated soils, root decay, the tree’s location on the side of a steep hill, and what appeared to be most of the branching on the line-side of the canopy, where the primary reasons for the tree’s failure. There were also some pet graves located at the base of the tree and may have been contributing factors but not significantly so. | Hilde Edmunson at 1753 Carriage Ln said she did not see the tree fail. But was home and heard a loud bang. | Tree was cleared of the lines by a Davey crew during a District Callout Request made at 2:30 am that morning. | 2020-03-20 14:20 | 2016-06-28
OUTAGE ID NUMBER: 160630E99479 | DISTRICT NAME: | 654 | 859 | 2407 EL CORTO DR, VISTA 92084 | Pine | 2016-06-30 | QQ3475 | P17326 P758251 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 8.0 to 9.9 ft | Non-SDGE Crew Caused | 2016-01-11 | Y | 10.0 to 11.9 ft | N | 2010-04-08 | N | 40.1 to 50 ft | Unable to Verify | 18.0 to 23.9 in | Other | 15.1 - 20 | No Record |  | None |  | No Record | No Record | N | A third party contractor, performing a removal of a pine tree (Tree ID QQ3475) dropped a branch or top from the canopy of a Pine tree into the primary facilities bringing down the primary and damaging two poles. Both poles were older and damaged during this event so they were both replaced. No report of fires or injuries. | The property owner (Tracy Rigsby 760 458-6773) witnessed the event and said “the tree fell strait down”. An interview with the responsible party (Mario Godinez 760 803-5812 – who is not associated with the reported tree company on scene Southwest Tree Service) revealed that he had topped the tree or branch (he was hard to understand and used both words to describe the limb), using a rope and it fell into the lines. He was not hurt but “very scared”. In an interview with the owner of Southwest Tree Service (Steve Elesky 858 335-4650) he stated that the work was not part of his company but the work of an employee, authorized by him to borrow his truck to chip the brush for a friend who was performing the removal. So he said his company and employees, during working hours, were not involved. | The tree trunk is still standing so we will pursue removal of this and others at the property. The property owner is agreeable. | 2020-03-20 14:20 | 2016-07-06
OUTAGE ID NUMBER: 160709E99995s | DISTRICT NAME: | 518 | 1437 | 425 BANCROFT ST, SAN DIEGO 92102 | Eucalyptus | 2016-07-09 11:35 | AQ660 | P739217 P733225 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-08-03 | N | 10.0 to 11.9 ft | N | 2015-11-12 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A small "flyer" / twig detached off an inventory Eucalyptus (AO660), fell onto primary wire, and must have slid down phase to transformer on P739203 where it cross pahsed at point where conductor clearance is minimal (12-18") between phases. Euc tree sits about 100ft West and uphill of where it cross pahsed. There were other small Euc "flyers" on the Tel-Co lines at pole. No direct evidence (burned foliage) could be found at base of pole on AF investigation of 7-11-16. | Respondindg ETS Jake Stiles (619.247.3920) confirms he pulled burned Euc "flyer" off high side bushings on transformer at P739203. He stated the vegeation material (estimated to be 1/4" x 18") was burned up and fell apart when handled. | Inventory Eucalyptus AO660 is clear and compliant at 10 to 12 ft to side. It is manged by VMS and will be evaluated annually and trimmed as needed. | 2020-03-20 14:20 | 2016-07-15
OUTAGE ID NUMBER: 16072E100845s | DISTRICT NAME: | 458 | 356 | 345 SILVERBROOK DR, EL CAJON 92019 | Oak | 2016-07-21 04:12 | PS2555 | P774355 P176435 | 312 - Flashover/vegetation | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft |  | 2015-12-09 | N | 10.0 to 11.9 ft | N | 2015-03-19 | Y | 20.1 to 30.0 ft | 8.0 to 9.9 ft | 8.0 to 12.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A very small twig or branch (estimated 1/4" x 12-18") was found on high side bushings at transformer on P774355 . Responding ETS cleared vegetation and refused the circuit. AF investigating outage finds dead Hawk in tree canopy under transformer. There is a possibility this was an electroctioin of Hawk. Area Forester forwards locaton to Environmnental Dept for reporting. Responding ETS only saw small piece of vegetation (darkness) on high side bushings at transformer. He did not see hawk and was not coded as such. | N/A | This locaton was forwarded to Environmental Dept to evaluate for Avian Protection on this facility. | 2020-03-20 14:20 | 2016-08-08
OUTAGE ID NUMBER: 160731E101667 | DISTRICT NAME: | 384 | 230 | 2866 RECHE RD, FALLBROOK 92028 | Oak | 2016-07-31 | VF2399 | P418314 P418313 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-04-12 | N |  | Y |  | N | 40.1 to 50 ft | Unable to Verify | 36.0 to 41.9 in | None | 20.1 - 30 | No Record |  | Heart Rot |  | Co-dominant Branch | Included Bark | N | A medium sized Oak failed at the base (codom with included bark) and fell across the driveway and struck the pole / downguy, damaging two poles and bringing the lines down. The tree showed signs of topping in the past. A small 18ftx40ft fire was extinguished by the fire dept. The property is vacant but an adjacent owner gave me the owner’s info as John Brackett, Big Block Realty 760 301-5311. | The property owner at 2868 Reche Rd, Tom Guth (760 723-2721), said the weather was hot and clear, no winds, and that a person at the park (Live Oak Park) noticed the fire and came to the property. Mr. Guth tried to hose down the grass during the fire and I explained to him the dangers; he wasn’t fully aware. | Mr. Guth was agreeable to a small removal project at his property. No further work required on the outage tree (a Davey crew was called out to clear debris during the outage). | 2020-03-20 14:20 | 2016-08-01
OUTAGE ID NUMBER: 160801E101679s | DISTRICT NAME: | 456 | 387 | 634 CREST DR, EL CAJON 92019 | Palm-Fan | 2016-08-01 07:14 | GD4468 | P471099 P471098 | 704 - Line fault/tree trimming | 326 - Palm frond contact | Private | Primary | 12.0 to 14.9 ft | Non-SDGE Crew Caused | 2015-10-29 | N | 15.0 to 19.9 ft | N | 2016-01-15 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 13.0 to 17.9 in | Other | 12.1 - 15 |  |  | None |  | No Record | No Record | N | Pieces of Palm fronds and husks were found on conductors and other high voltage hardware on riser pole P471099 and reported as cause for this outage. Responding ETS cleared and re-energized the circuit. Area Forester investigating this veg outage notices seed pods and frond husks had been cut, not naturally detached. AF investigates further and finds out Atlas Tree Service had been hired by property owner and had been trimming 15 nearby Mex Fan Palms on Friday 7-29-16. The veg outage occured in the early morning hours of Monday 8-1-16. It is believed thast the frond husk had been sitting on pothead for a couple of days dry. When conditions were just right (morning dew) the moisture caused the cross phase at pot head causing the outage. | Area Forester spoke to working GF for Atlas Tree Service, Dave Wolcutt (619-414-3682). He confirms Atlas Tree Service had been working the trees near by on Friday 7-29-16. He also confirms a few seed pods had laid on conductors. He did not see the small frond husk on the pot head that is suspected of casing this outage. | A meeting is planned to meet with Atlas Tree Service Mangement and SDG&E Vegetaton Management to review this incident. A phone call to SDG&E could have prevented this. | 2020-03-20 14:20 | 2016-08-08
OUTAGE ID NUMBER: 160818E103075 | DISTRICT NAME: | 381 | 234 |  | Eucalyptus | 2016-08-18 | CD19 | P10690 P112044 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | Unable to Verify | 8.0 to 12.9 in | None | 30.1 - 40 | No Record |  | Co-dominant Branch |  | Weak Branch Attachment | No Record | N | A large non-inventory, over-mature Euc had a 15in diameter leader fail into another smaller non-inventory Euc (8-10in DBH) causing it to fall from across the street and either struck the overhead conductor or struck the guy span and blew the fuse. The lines slapped together but did not come down. No fire or injuries were reported or observed. The tree with the original breakout was located over 60ft away from the wires but had a leader fall into another, thinner, smaller tree and it failed into the conductor in a domino effect. | The customer at 2140 Green Canyon (Robert Kruis 760 728-9394) said he recalled no weather or significant wind at the time of the event. The customer at 2242 (where the second tree was located) is owned by his daughter and son-in-law and he says both of them would be agreeable to a removal project at the properties. | No further work required on this tree but an Area Lead will be assigned to perform a reliability enhancement project in this immediate area (2-3 spans north and south of P112044) to remove several of these taller, thinner Eucs generating from the drainage area on the east side of the road. A similar project was performed several years ago in this area and it was successful but it is time to take another look into more removals. | 2020-03-20 14:20 | 2016-08-22
OUTAGE ID NUMBER: 160923E105834 | DISTRICT NAME: Northeast | 601 | SEA1 |  | Eucalyptus | 2016-09-23 | CE2810 | P61083 P61394 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 2.1 to 4.0 ft | 60.0 to 80.0 in | Other | 2.1 - 4 |  |  | Decayed Branch |  | No Record | No Record | N | A large branch approximatly 12-18in diameter broke out of tree at secondary end pole. The branch struck the telco shaking the poles and wires causing the outage three spans down. A small amount of decay was observed in the center of the branch. Decay was not observable and tree was several spans from primary so it wouldn't have been inspected for reliability. | Spoke to the customer at 1440 Crest that said she heard a loud pop and the power went out. Spoke to troubleman Troy Pierce that said the breakout was the cause of the outage. | I issued the tree for trim to eliminate potential for another breakout and outage | 2020-03-20 14:20 | 2016-11-03
OUTAGE ID NUMBER: 161109E109137s | DISTRICT NAME: Eastern | 520 | 719 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2016-11-09 | GW9425 | P186034 P82929 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2016-07-18 | N | 12.0 to 14.9 ft | N | 2014-09-30 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 60.0 to 80.0 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A small branch (estimated to be 1/2" x 4-6ft) detached off inventory Euc GW9425, laid on conducors at station pole P186034, cross phased in rain event, causing the outage on Cir 719 on 11/09/16. The cross phase caused branch to burn up on conductors. Small Euc branch was found at base of pole during AF investigation on 11/10/2016. | Adjacent property owner (no name given) heard a loud explosion and flash and calleed 911. | There are a line (12-18) of very tall inventory Eucalyptus trees that have been trimmed and maintained over the yesars by heavy "roll back" trims away from wires. This small piece of vegetation can be considered incidental. There would be no solution short of removing 12-18 very tall Eucalyptus trees in the area. They are on golf course (private property) removals have been declined. The trees act as a baracade for errant golf balls. The golf couse has been removing the dead and dying Eucs along this line through the years. VMS will inspect annually and trim trees as needed in the area. | 2020-03-20 14:20 | 2016-12-20
OUTAGE ID NUMBER: 161114E109460s | DISTRICT NAME: | 394 | 237 | 999 NEIGHBORLY LN, RAMONA 92065 | Eucalyptus | 2016-11-14 13:05 | CE2815 | P712244 P712243 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Non-SDGE Crew Caused |  | Y |  | N |  | Y | 40.1 to 50 ft | 30.1 to 40.0 ft | 8.0 to 12.9 in | Other | 30.1 - 40 |  |  | None |  | No Record | No Record | N | Friend of owner was removing Eucs leaning toward the lines. He cut back side of Euc and tree fell, striking both phases of primary cuasing fuse to blow. | Owner said he was home sick in bed and was awoken by friend that told him he was removing the tree and hit the wires. Owner called SDGE to report the outage. Spoke to troubleman that explained that the tree fell across both phases causing the fuse to blow. | No other trees in yard are being removed. Owner did agree to remove six palms directly below the primary during next routine. Owner said he was unaware friend was cutting trees and will not allow him to remove any other trees. | 2020-03-20 14:20 | 2016-11-17
OUTAGE ID NUMBER: 161121E109987s | DISTRICT NAME: | 365 | RA1 | 212 11TH ST, RAMONA 92065 | Eucalyptus | 2016-11-21 | CE2816 | P13082 P13083 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 15.0 to 19.9 ft | 18.0 to 23.9 in |  | 40.1 - 50 |  |  | Dead Branch |  | No Record | No Record | Y | During a storm event, a dead branch detached from a green Eucalyptus and blew on to a bottom stack of primarys. The branch was approx. 36in long and 1/2in diameter. the branch cross phased the primary and caused the fuse to blow. | Spoke to responding troubleman Ruben Diaz. He said the branch broke out of the tree and blew onto the bottom stack of primarys between P13082 & P113883 and caused the fuse to blow. | The tree will be issued on a memo to reduce the crown and mitigate the hazard. | 2020-03-20 14:20 | 2016-11-29
OUTAGE ID NUMBER: 161216E111311s | DISTRICT NAME: Northeast | 305 | 788 | 2103 MOUNTAIN VIEW DR, ESCONDIDO 92027 | Eucalyptus | 2016-12-16 | FJ3129 | P610551 P610550 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Secondary | 10.0 to 11.9 ft | Non-SDGE Crew Caused | 2016-02-20 | Y | 10.0 to 11.9 ft | N | 2016-05-23 | Y | 20.1 to 30.0 ft | 8.0 to 9.9 ft | 42.0 to 47.9 in | Other | 15.1 - 20 |  |  | None |  | No Record | No Record | N | Third party tree trimmer was trimming a Eucalyptus tree when a branch fell onto the primary. the lines are vertical in the span effected and the branch pushed the phases togehter causing the fuse to blow. | Owner said it was a friend of his landscaper that was trimming when the outage happened. Said he didn't know his name. | Owner is allowing removal of another Euc in the inventory, (FJ3130) and removal of the front lead in the tree that caused the outage. | 2020-03-20 14:20 | 2016-12-21
OUTAGE ID NUMBER: 161223E112167 | DISTRICT NAME: | 210 | 51 | 2812 POINSETTIA DR, SAN DIEGO 92106 | Palm-Fan | 2016-12-23 | FM18359 | P37104 P837943 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 20.0 to 30.0 ft | Tree Failure | 2016-10-19 | N | 20.0 to 30.0 ft | N | 2016-01-27 | N | 60.1 to 80 ft | 20.0 to 30.0 ft | 13.0 to 17.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Palm frond detached from palm and cross phased primary conductors and blew the fuse. | Customer Lanita Carroll said she heard a loud bang and the power went out. She said she was cleaning up the palm debris the next day and found a seed pod with burn marks. She said she is willing to remove but thinks the city owned them. Gave info to Dan Bohnett to follow up. | Palms were listed for trim. Sent tree crews to site after investigation to due annual trimming. | 2020-03-20 14:20 | 2017-01-05
OUTAGE ID NUMBER: 161224E112172s | DISTRICT NAME: | 521 | 941 | 703 1ST AVE, CHULA VISTA 91910 | Palm-Fan | 2016-12-24 | PL2278 | P83940 P83939 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2016-07-21 | N | 8.0 to 9.9 ft | N | 2016-09-29 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 8.0 to 12.9 in |  | 10.1 - 12 |  |  |  |  | No Record | No Record | N | Palm was trimmed in September and had no dead fronds or seed pods but the palm husks are sheding and fell onto the lower stack of primarys. Three phases of the lower primarys have only 1ft of spread between the wires. | Customer at this address doesn't speak english | I am going to issue a memo to remove all loose husks above line level to eliminate potential. Will try to send spanish speaking crew and or GF to speak to customer about removal | 2020-03-20 14:20 | 2016-12-29
OUTAGE ID NUMBER: 161224E112188s | DISTRICT NAME: | 651 | 66 | 15515 LAS PLANIDERAS, RANCHO SANTA FE 92067 | Eucalyptus | 2016-12-24 | CE2819 | P19837 P19838 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 40.1 to 50 ft | 20.0 to 30.0 ft | 18.0 to 23.9 in |  | 30.1 - 40 |  |  | None |  | No Record | No Record | N | A branch approx 3in in diameter and 6ft long broke out of tree during high winds and fell accross the cutouts on P19837. Branch was gone by the time of investigation but breakout in top of tree doesn't appear to have decay. | Responding troubleman Dan Doyle said branch was green. Cause is limb breakout due to high winds. No customer home in area to get statement. | I will add tree to routine for reliability work. | 2020-03-20 14:20 | 2016-12-30
OUTAGE ID NUMBER: 161231E112526s | DISTRICT NAME: | 362 | 351 | 26860 N BROADWAY, ESCONDIDO 92026 | Eucalyptus | 2016-12-31 | CE2820 | P239062 P115773 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 60.1 to 80.0 ft | 36.0 to 41.9 in |  | 60.1 - 80 |  |  |  |  | No Record | No Record | N | Large non inventory Euc uprooted and fell accross conductors bringing inside phase down. Tree is on the edge of a water course and ground was saturated from recent rains. The wind and rain event caused the tree to uproot. | Customer Ed Bosworth said tree uprooted and was laying accross the road | Will send DRG in to evaluate potential for other Eucs in the area for reliability work. | 2020-03-20 14:20 | 2017-01-05
OUTAGE ID NUMBER: 170113E113369s | DISTRICT NAME: | 221 | 835 | 5131 DEL MAR MESA RD, SAN DIEGO 92130 | Eucalyptus | 2017-01-13 | IT4562 | P95889 P95889 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2016-06-08 | N | 10.0 to 11.9 ft | N | 2015-08-28 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | None | 15.1 - 20 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | A very small Eucalyptus "flyer" / twig estimated to be 1/4" x 12-18" detached from nearby inventory Eucalyptus IT4562, fell onto lightning arrestor on cable pole P95889 causing primary outage on Cir 835. Responding ETS cleared and re-fused and it held. | Nearby resident heard a loud boom in the midddle of the night. | Trees in the area are clear and compliant. They are evaluated annually and trimmed as needed. | 2020-03-20 14:20 | 2017-01-18
OUTAGE ID NUMBER: 170120E113735 | DISTRICT NAME: | 623 | 288 | 602 RANCHO SANTA FE RD, ENCINITAS 92024 | Pine | 2017-01-20 | CE2825 | P517948 P517949 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 15.0 to 19.9 ft | 13.0 to 17.9 in |  | 15.1 - 20 |  |  |  |  | No Record | No Record | N | Non-inventory Pine uprooted and fell accross the primary bringing the lines down. Cause is high winds and saturated soil. Root base appears smaller than normal. | Spoke to Marion at 2250 9thSt. She said neighbor called her and said one of our wires was hanging low along span on her street. She said right after that she heard an explosion and the power went out. | Left a message with customer asking that he call me back in regards to two other pines that may be a hazard. | 2020-03-20 14:20 | 2017-02-03
OUTAGE ID NUMBER: 170120E113781 | DISTRICT NAME: | 412 | 731 | 4255 CONRAD DR, SPRING VALLEY 91977 | Eucalyptus | 2017-01-20 | AR864 | P570524 P777765 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2016-09-13 | N | 10.0 to 11.9 ft | N | 2016-11-18 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | Inventory Eucalyptus toppled into others and made contact with primary causing wire down and outage on Cir731 in a severe weather event. | n/a | Tree has toppled, no further work required. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113785 | DISTRICT NAME: | 456 | 410 | 1533 SKYLINE LN, EL CAJON 92019 | Jacaranda | 2017-01-20 | AD1983 | P192109 P178304 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-10-19 | N | 12.0 to 14.9 ft | N | 2016-01-28 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  |  |  | No Record | No Record | N | A limb estimated to be 1" x 6-8ft detached off an inventory Jacaranda and fell onto primary in severe weather event. | N/A | Tree looks OK / healthy and is managed by VMS. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113786 | DISTRICT NAME: | 456 | 96 | 1671 VISTA GRANDE RD, EL CAJON 92019 | Pine | 2017-01-20 | JK77 | P100137 P774748 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 30.1 to 40.0 ft | 24.0 to 35.9 in |  | 40.1 - 50 |  |  | Co-dominant Branch |  | No Record | No Record | N | A large non-inventory Alleppo Pine failed at co-dominate trunk union, hit primary, causing a momentary outage in severe weather event. | N/A | This tree is on the ground. Other in area check out OK. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170120E113789 | DISTRICT NAME: | 410 | 549 | 676 EL MONTE RD, EL CAJON 92020 | Palm-Feather | 2017-01-20 | RX649 | P378463 P770272 | 428 - Palm tree contact due to storm/wind | 428 - Palm tree contact due to storm/wind | Private | Primary | 4.1 to 5.9 ft |  | 2017-01-12 | N | 10.0 to 11.9 ft | N | 2016-04-14 | Y | 20.1 to 30.0 ft | 4.1 to 5.9 ft | 8.0 to 12.9 in |  | 10.1 - 12 |  |  |  |  | No Record | No Record | N | An frond from inventory Queen Palm made contact with conductors during a severe weather event causing outage on Cir 549 |  | Tree contractor (UTS) was called out to clear tree and ended up removing this tree during the night of the call out. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113795 | DISTRICT NAME: | 309 | 470 | 16088X OLD MILKY WY, ESCONDIDO 92027 | Eucalyptus | 2017-01-20 | CE2821 | P419532 P419532 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 80.1 to 200 ft | 100.1 ft + | 54.0 to 59.9 in |  | 100.1 - '+' |  |  | Root Rot |  | No Record | No Record | N | Large non inventory Euc uprooted and fell accross wires between P419532 - P419531. Tree showed signs of root rot. |  | Will have DRG inspect for other potential hazards. | 2020-03-20 14:20 | 2017-02-09
OUTAGE ID NUMBER: 170120E113796 | DISTRICT NAME: | 456 | 96 |  | Eucalyptus | 2017-01-20 | JK75 | P578588 P578589 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind |  | Primary |  | Tree Failure |  | N |  | N |  | N | 60.1 to 80 ft | 30.1 to 40.0 ft | 8.0 to 12.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | non-inventory Eucalyptus estimated to have been 8-12" x 60ft toppled at base in severe weather causing an outage on Cir 96. |  | Tree has toppled and no longer a threat. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113797 | DISTRICT NAME: | 302 | 595 | 303X RICHMAR AVE, SAN MARCOS 92069 | Pine | 2017-01-20 | CE2824 | P119288 P12640 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 2.1 to 4.0 ft | 13.0 to 17.9 in |  | 2.1 - 4 |  |  |  |  | No Record | No Record | N | Non inventory pine uprooted and struck pole to pole secondary snapping stub and secondary pole. This caused the primarys on pole P10532 to slap together causing the fuses to blow. |  | No follow up required, no more trees in span | 2020-03-20 14:20 | 2017-02-09
OUTAGE ID NUMBER: 170120E113810 | DISTRICT NAME: | 520 | 719 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2017-01-20 | FR6463 | P82931 P186034 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2016-07-18 | N | 10.0 to 11.9 ft | N | 2015-10-27 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A large limb estimated to be 6" x 12ft detached off an inventory eucalyptus and fell onto conductors. There were several Eucs that shed large limbs at about the same time during a severe weather event. |  | All the large Eucalyptus on this golf course have been "rolled back" as far as possible. An offer to assist in removing these large trees was made to golf corse superintendant. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113812 | DISTRICT NAME: | 520 | 256 |  | Pepper-Brazilian | 2017-01-20 | JK83 | P250440 P188904 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 404 - Circuit flashover/storm/high winds (undetermined) |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 80.1 to 100.0 ft | 24.0 to 35.9 in |  | 80.1 - 100 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb shed off a non-inventory Brazzillian Pepper tree located in backyard of 683 Garret Ave. The limb hit pole to pole guy wires at span P250440 to P188904. The impact caused conductors to fall one span away at P188904 to P831558. Live wires may have caused a structure fire. Chula Vista FD was called to site to supress structure fire. | News media (KUSI) was on site filming incident for local nightly news where it aired. | No further work was required. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170120E113814 | DISTRICT NAME: | 520 | 154 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2017-01-20 | FR6371 | P726350 P726351 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-07-18 | N | 10.0 to 11.9 ft | N | 2016-10-05 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 42.0 to 47.9 in |  | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | a large limb estimated to be 8-10" x 12-16ft detached off inventory Eucalyptus tree and fell onto conductors causing wire down and outage. |  | This tree and others hin the area have been "rolled back as far as possible. High winds pushed the limb into wires. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113824 | DISTRICT NAME: Metro | 552 | 341 | 3985 ALTA LOMA DR, BONITA 91902 | Eucalyptus | 2017-01-20 | JK85 | P83465 P87745 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 420 - Tree contact due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 40.1 to 50 ft | 30.1 to 40.0 ft | 36.0 to 41.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | A powerful Pacific storm wreaked havoc on this particular circuit. There were multiple reported causes for this outage with 4-5 locations given in 01/20/2017 DSOR with wires down. Each given location was investigated by Area Forester. Only one of these reported locations involved a tree. Cause #6 in this DSOR reports of wire down in span (P83654 - P87745). In this span was a Eucalyptus tree failure. A very large non-inventory tree failed at root base due to high winds and rain, hit primary wire causing wire down, and contributed to outage on Cir 341. There were 4 other locations in DSOR that had wires down. Each location was investigated and this was the only span that had a tree failure. Eucalyptus was estimated to be about 36" x 60ft tall and failed at base. This tree also may have played a part on another outage on this Cir a few days later. Outage #170122E11370 on 1/22/2017 DSOR uses the same verbiage and gives the same span as above. It is thought that the second outage was taken to re-energize the damaged span from original tree failure for outage # 170120E113824 from (01/20/2017). | N/A | This tree had failed and is no longer a threat. | 2020-03-20 14:20 | 2017-03-07
OUTAGE ID NUMBER: 170120E113834 | DISTRICT NAME: | 212 | 56 | 4449 OCEAN BLVD, SAN DIEGO 92109 | Palm-Fan | 2017-01-20 | PZ40 | P2302369122 P2302369122 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2016-12-21 | N | 10.0 to 11.9 ft | N | 2016-03-30 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A seed pod or frond detached from in ventory Mex Fan Palm causing the outage on Cir56 during a severe weather event. | N/A | Private inventory tree is managed by VMS and a offer to remove has been made. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113838 | DISTRICT NAME: | 454 | 73 | 22152 FUSCO LN, ALPINE 91901 | Pine | 2017-01-20 | SF2976 | P139487 P139486 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2017-01-04 | N | 10.0 to 11.9 ft | N | 2016-04-20 | Y | 40.1 to 50 ft | 6.0 to 7.9 ft | 18.0 to 23.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | An inventory Pine tree failed at base in severe weather event. The whole tree failure had a direct hit to primary pole P274899 causing snapped pole and wires down. | N/A | Whole tree failure, no follow up required. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170120E113848 | DISTRICT NAME: | 466 | 442 | 4861 CORTE MADERA RD, PINE VALLEY 91962 | Pine | 2017-01-20 15:28 | FY1285 | P274899 P274900 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2016-09-21 | N | 10.0 to 11.9 ft | N | 2013-12-19 | Y | 30.1 to 40 ft | 8.0 to 9.9 ft | 54.0 to 59.9 in |  | 15.1 - 20 |  |  | Co-dominant Branch |  | No Record | No Record | N | A large inventory Pine with co-dominate trunk had one co-dominate trunk fail in severe weather event, hit pole causing pole to snap and outage. | N/A | The remaining top of tree and another co-dominate Pine tree (FY1282) was toppped / made safe before next approaching storm. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170120E113861 | DISTRICT NAME: | 521 | 255 | 130 MINOT AVE, CHULA VISTA 91910 | Pine | 2017-01-20 | EB216 | P80808 P80809 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-07-13 | N | 10.0 to 11.9 ft | N | 2016-10-06 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 18.0 to 23.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | A large Alleppo Pine failed at base, struck and brought wires down causing the outage on Cir 255 in severe weather event. |  | Whole tree failure requires no follow up trim. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113864 | DISTRICT NAME: Eastern | 302 | 599 | 197X VIA LAS BRISAS, SAN MARCOS 92069 | Eucalyptus | 2017-01-20 | CE2822 | P811694 P32681 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 20.0 to 30.0 ft | 13.0 to 17.9 in |  | 30.1 - 40 |  |  | None |  | No Record | No Record | N | Large non inventory Euc uprooted due to heavy rains and winds. The tree was on a hillside sloping down towards the lines. The rains saturated the soil and the winds helped push the tree over contacting the primary bringing both phases down. | neighbor said the winds were blowing very hard when she heard a loud bang and the power went out. | There are several other Eucs on the hillside that may require work. I'm going to have DRG inspect the area to identify any other potential hazards, | 2020-03-20 14:20 | 2017-02-02
OUTAGE ID NUMBER: 170120E113871 | DISTRICT NAME: | 520 | 719 | 933X MADISON AVE, CHULA VISTA 91911 | Palm-Date | 2017-01-20 | QJ4499 | P83860 P88967 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 8.0 to 9.9 ft |  | 2016-07-14 | N | 10.0 to 11.9 ft | N | 2012-09-18 | Y | 40.1 to 50 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A frond detached off an inventory Canary Island Date Palm in a severe weather event , made contact with conductors, causing the outage. |  | this inventory tree is managed by VMS. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113874 | DISTRICT NAME: | 521 | 941 | 190 E I ST, CHULA VISTA 91910 | Eucalyptus | 2017-01-20 | EB2223 | P187088 P187087 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-07-26 | N | 10.0 to 11.9 ft | N | 2016-09-12 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 42.0 to 47.9 in |  | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A large limb estimated to be 4" x 16ft detached off an inventory Euc and fell onto conductors in a severe weather event causing the outage. | N/A | This inventory tree appears healthy, is clear and compliant, and is managed by VMS. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113876 | DISTRICT NAME: | 463 | 157 |  | Oak | 2017-01-20 | JK76 | P277826 P970162 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 40.1 to 50.0 ft | 24.0 to 35.9 in |  | 40.1 - 50 |  |  |  |  | No Record | No Record | N | A large non-inventory Oak tree toppled at base in severe weather event, hit primary causing wires down and outage. The backside holding roots located along seasonal creek suffered from severe erosion due to heavy rains. |  | Whole tree failure requires no further work. | 2020-03-20 14:20 | 2017-03-03
OUTAGE ID NUMBER: 170120E113937 | DISTRICT NAME: | 520 | 1202 | 2175 CACTUS RD, SAN DIEGO 92154 | Other-Slow | 2017-01-20 | JK84 | P89060 P188598 | 402 - Circuit flashover/fog/foreign object | 428 - Palm tree contact due to storm/wind | Private | Primary |  |  |  | N |  | N |  | Y | 0.0 to 5.0 ft | 30.1 to 40.0 ft | 0.0 to 2.9 in | [6 empty] | No Record | No Record | N | The 1.20.2017 DSOR states "Palm Frond Contact" as the cause for this outage. There are no Palms in immediate area (with in 1/4 mi). At this location, there were a lot of Tumleweeds pushed by winds in the corner of large fenced car impound yard where the given Pole P247353 is located. With the high winds of the 1.20.2017 storm, it is highly likely that a loose Tumbleweed may have been pushed by strong winds up into conductors at this location causing the outage. | N/A | Recomend to change cause code from 428 "Palm Frond Contact" to 402 "Circuit flash over -foreign object" | 2020-03-20 14:20 | 2017-03-07
OUTAGE ID NUMBER: 170121E113921 | DISTRICT NAME: | 408 | CMP1 | 9267 EDGEWOOD DR, LA MESA 91941 | Pepper (California) | 2017-01-21 | AR4190 | P174169 P474619 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 404 - Circuit flashover/storm/high winds (undetermined) | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-01-28 | N | 10.0 to 11.9 ft | N | 2016-06-03 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 36.0 to 41.9 in |  | 8.1 - 10 |  |  |  |  | No Record | No Record | N | A previously topped / dead California Pepper toppled in severe weather event. The wide spread side branched hooked Tel-Co wires, shook poles, and caused a primary outage on Cir CMP1. | UTS was called out to this location during the storm. | Tree is on the ground requiring no further work. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170122E113960 | DISTRICT NAME: | 210 | RV1 | 1432 CARLETON SQ, SAN DIEGO 92106 | Palm-Feather | 2017-01-22 | SF31 | P732360 P2062169747 | 428 - Palm tree contact due to storm/wind | 428 - Palm tree contact due to storm/wind | Private | Primary | 4.1 to 5.9 ft | Tree Growth | 2016-10-14 | Y | 10.0 to 11.9 ft | N | 2016-02-10 | N | 30.1 to 40 ft | 0.0 to 2.0 ft | 13.0 to 17.9 in |  | 15.1 - 20 |  |  |  |  | No Record | No Record | N | A Palm frond from an inventory Queen Palm (SF31) made contact with 4kv conductors in severe weather event. | N/A | This palm was cleared during the outage restoration. This private property Palm belongs to sensative customer who has historically not allowed tree trim contractor to obtain full clearqance through the years. Area Forester will follow up with customer and discuss the need to remove these palms for safety. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170122E113970 | DISTRICT NAME: | 552 | 341 | 3985 ALTA LOMA DR, BONITA 91902 | Eucalyptus | 2017-01-22 | JK85 | P83465 P87745 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 40.1 to 50 ft | 30.1 to 40.0 ft | 36.0 to 41.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | A large non-inventory failed at base in severe weather causing an outage in span P83654 - P87745. It is thought this tree failed during initial 1/20/2017 storm and contributed to large Cir 341 outage #170120E113824 on 01/20/2017. This initial outage on 1/20/2017 was very extensive with muliple locations of wires down. There is a possiblity that this tree fell during 01/20/2017 event caused outage # 170120E113824. Line crews may have kept this singel span de-energized in interest of restoring residential homes as a pririority (this location is horse stables). A second outage (this one) may have been taken to re-energize this span over horse stables. The original cause was the tree failure on 1/20/2017 with in very same span. | worker at stables stated electricity was off "for days" until weather heads got | Whole tree failure requires no follow up tree trim. | 2020-03-20 14:20 | 2017-03-07
OUTAGE ID NUMBER: 170122E113972 | DISTRICT NAME: | 520 | 154 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2017-01-22 | GP244 | P88388 P88387 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 15.0 to 19.9 ft | Tree Failure | 2016-07-18 | N |  | N |  | Y | 60.1 to 80 ft | 15.0 to 19.9 ft | 24.0 to 35.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A powerful pacific storm pushed this tree along with 3-4 other non-inventory Eucalyptus into each other. The trees dominoed into primary wires near P88388 causing wires to come down during severe weather. | N/A | An offer to assist in removing several large trees on golf course was made to GC Superintendant. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170122E114004 | DISTRICT NAME: | 302 | 599 | 135 SUNSHINE LN, SAN MARCOS 92069 | Pine | 2017-01-22 | TH2327 | P613984 P613984 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-06-08 | N |  | N |  | Y | 40.1 to 50 ft | 4.1 to 5.9 ft | 18.0 to 23.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Large inventory Pine uprooted due to rain and wind event. Soil around base was saturated and was unable to anchor tree in the wind. The pine uprooted and layed on a fork lift parked next to it. The fork lift stopped the tree from falling completely but it did lay on top of the pole and wires causing the outage. |  | No other work required. The subject pine and another pine just to the west was removed | 2020-03-20 14:20 | 2017-02-02
OUTAGE ID NUMBER: 170122E115345 | DISTRICT NAME: | 210 | RV1 | 1552 LOCUST ST, SAN DIEGO 92106 | Pepper (California) | 2017-01-22 | GA6140 | P934010 P934050 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-10-10 | N | 10.0 to 11.9 ft | N | 2017-01-13 | Y | 20.1 to 30.0 ft | 2.1 to 4.0 ft | 36.0 to 41.9 in |  | 8.1 - 10 |  |  |  |  | No Record | No Record | N | An inventory Ca Pepper (GA6140) was reported to have caused phases to be pushed together causing loose wire hanging according to 1-22-2017 DSOR report. | N/A | Area Forester checked location, but tree has since beeen cleared. It was judged that this could have been the cause of the outsage due to close proximity of this tree before it was trimmed. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170124E114163 | DISTRICT NAME: | 352 | 788 | 1622 S CITRUS AVE, ESCONDIDO 92027 | Eucalyptus | 2017-01-24 | RZ1106 | P314884 P314885 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 15.0 to 19.9 ft | Tree Failure | 2016-07-07 | N | 12.0 to 14.9 ft | N | 2012-08-24 | Y | 60.1 to 80 ft | 15.0 to 19.9 ft | 36.0 to 41.9 in |  | 30.1 - 40 |  |  | Root Rot |  | Heart Rot | Co-dominant Branch | Y | Large multi trunk inventory Euc had one trunk split out and fall on stub pole P249633s snapping it in half. The tree was laying heavy on the guy and the troubleman did a force outage opening jumpers and fuses to de-energize the primary overhead. The Euc had two co-dominant trunks that had root and heart rot. With recent rains and winds, the soil around the tree was saturated and due to the other issues, the tree failed. |  | I'm going to issue the tree to contractors to top the tree to safe height. The root and heart rot is present in the other trunk and has a large hole in the ground next to the trunk from the uproot of the other side. | 2020-03-20 14:20 | 2017-02-02
OUTAGE ID NUMBER: 170127E114473 | DISTRICT NAME: | 514 | 167 | 6350 COLLEGE GROVE DR, SAN DIEGO 92115 | Other-Medium | 2017-01-27 | JK79 | P167293 P167292 | 402 - Circuit flashover/fog/foreign object | 402 - Circuit flashover/fog/foreign object | City | Primary |  | Tree Failure |  | N |  | N |  | Y | 5.1 to 15.0 ft | 30.1 to 40.0 ft | 0.0 to 2.9 in |  | 40.1 - 50 |  |  |  |  | No Record | No Record | N | DSOR reports "debris at P167293". Area Forester follow up confirms small vegetation with contact burns found at base of pole. It appears that small vegetation debris probabaly thrown by strong winds up onto energized riser pole where particular hardware has phases relatively close together. |  |  | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170127E114502 | DISTRICT NAME: | 513 | 1435 |  | Eucalyptus | 2017-01-27 | JK78 | P231096 P231482 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 80.1 to 200 ft | 40.1 to 50.0 ft | 36.0 to 41.9 in |  | 60.1 - 80 |  |  |  |  | No Record | No Record | N | A very large Eucalyptus (24"dbh x 125ft tall) was pushed by strong winds uphill and across street, hit conductors, causing wire down, and outage. Area Forester observed that there was almost no root plate and the sorrounding soil was extremely sturated. | N/A | This tree had failed and was on the ground. Other trees in area where inspected and determined not be a threat to wires at this time. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116081 | DISTRICT NAME: | 521 | HP1 | 60 E DONOHOE ST, CHULA VISTA 91911 | Pine | 2017-02-17 | EB2651 | P183032 P183031 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 2.1 to 4.0 ft | Tree Failure | 2016-07-15 | N | 10.0 to 11.9 ft | N | 2016-09-15 | Y | 20.1 to 30.0 ft | 10.0 to 11.9 ft | 18.0 to 23.9 in |  | 12.1 - 15 |  |  |  |  | No Record | No Record | N | The top portion of inventory Alleppo Pine snapped in severe weather, hit primary, causing the outage on Cir HP1. | N/A | Broken portion of tree is below conductors on private property. Tree is managed by VMS. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116088 | DISTRICT NAME: Eastern | 210 | 480 |  | Palm-Feather | 2017-02-17 | JK80 | P735163 P931430 | 428 - Palm tree contact due to storm/wind | 428 - Palm tree contact due to storm/wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 20.1 to 30.0 ft | 30.1 to 40.0 ft | 3.0 to 7.9 in |  | 20.1 - 30 |  |  | None |  | No Record | No Record | N | A non-inventory Fishtail palm toppled into secondary wires during storm event and caused outage on primary Cir 480. Palm was located in private backyard of 3750 Dudley St SD | N/A | Whole Plam tree failure requires no furhter follow up work. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116089 | DISTRICT NAME: Orange County | 702 | 792 | 34681 CALLE LOS ROBLES, CAPISTRANO BCH 92624 | Eucalyptus | 2017-02-17 | ET896 | P25631 P125669 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Distribution with Secondary Underbuild | 6.0 to 7.9 ft |  | 2016-07-13 | N | 10.0 to 11.9 ft | N | 2016-10-07 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Small branch material from the mature eucalyptus shed during high wind and rain conditions and landed on relatively close-spaced electrical facilities causing the primary outage. This same tree was also the source of a previous outage (170120E113732). |  | Customer has agreed to extensive pruning to roll back the tree canopy which should reduce the likelihood of an outage recurrence. Work is scheduled for 3/3/17. | 2020-03-20 14:20 | 2017-02-23
OUTAGE ID NUMBER: 170217E116093 | DISTRICT NAME: | 520 | 719 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2017-02-17 | FR6464 | P82931 P186034 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 8.0 to 9.9 ft |  | 2016-07-18 | N | 10.0 to 11.9 ft | N | 2015-10-27 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A tree limb shed off a very large inventory Eucalyptus due to severe wind and rain, laid across all three phases of primary causing the outage on Cir 719. |  | All the 100ft+ eucalyptus trees near SDG&E primaries on this golf course have been "laid back" as far as possible. The high winds and rain caused a branch to detach and the high winds pushed the limb toward conductors. An offer to assist in removing the large Eucalyptus trees was made to the Golf Course Superintendant. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116096 | DISTRICT NAME: | 403 | 730 | 1709 CANYON RD, SPRING VALLEY 91977 | Eucalyptus | 2017-02-17 | BC3074 | P671722 P675852 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 20.0 to 30.0 ft | 18.0 to 23.9 in |  | 60.1 - 80 |  |  |  |  | No Record | No Record | N | This particular Eucalyptus (BC3074) was identifid by Pre-Inspector as a green reliability (GR) tree earlier in the day on 2/17/2017. A lean and exposed roots were identified as the defects in tree. This tree fell later in the day due to severe winds and rain. | N/A | Many other trees on this property have been identified for routine and GR trims. The trees will be trimmed in upcoming routine VMA tree trim schedule. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116103 | DISTRICT NAME: | 652 | 305 | 5424 EL SECRETO, RANCHO SANTA FE 92067 | Eucalyptus | 2017-02-17 | CE2826 | P211739 P211738 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 60.1 to 80.0 ft | 24.0 to 35.9 in |  | 60.1 - 80 |  |  |  |  | No Record | No Record | N | Large non-inventory Euc approx. 70ft from conductors uprooted and fell accross the road and struck the primarys and caused wire down. Root system was healthy. Tree was on hillside and failed due to saturated soil and high winds. | Spoke to Arnold Keene, (Rancho Association) He is concerned with other trees in the area. | I will evaluate the area and issue any work required for safety. | 2020-03-20 14:20 | 2017-02-23
OUTAGE ID NUMBER: 170217E116114 | DISTRICT NAME: | 514 | 362 |  | Ash | 2017-02-17 | JK81 | P734274 P734297 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 404 - Circuit flashover/storm/high winds (undetermined) |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 80.1 to 100.0 ft | 24.0 to 35.9 in |  | 80.1 - 100 |  |  | Heart Rot |  | No Record | No Record | N | A large portion of mature Ash tree located at 3333 North Montainview Dr broke off the main trunk due to high winds and rain, hit pole to pole guy wires (P734274 to P734297 ) causing several poles and wires to come down in the area. | N/A | Tree was made safe as storm call out requiring no further work. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116117 | DISTRICT NAME: | 210 | 482 | 3524 LOWELL WY, SAN DIEGO 92106 | Pine | 2017-02-17 | AQ3678 | P934441 P934438 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-10-11 | N | 4.1 to 5.9 ft | N | 2017-01-27 | Y | 40.1 to 50 ft | 4.1 to 5.9 ft | 24.0 to 35.9 in |  | 10.1 - 12 |  |  | Previous Branch Crack |  | No Record | No Record | N | A big crack developed due to strong winds on a large limb of an inventory Torrey Pine casuing limb to make contact with primary wires causing an outage. |  |  | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170217E116122 | DISTRICT NAME: | 212 | PB1 |  | Eucalyptus | 2017-02-17 | JK82 | P203188 P37795 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 404 - Circuit flashover/storm/high winds (undetermined) |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 80.1 to 100.0 ft | 18.0 to 23.9 in |  | 80.1 - 100 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A large limb detached off a non-inventory Lemon Gum Eucalyptus, hit pole to pole guy wire at span P203188 to P37795, caused wire to drop one span away at to P837160 to P37795. The wire down was arcing and sparking for an extended amount of time during the storm. | News media on scene recording live shots of wire down arcing and sparking. | Remaining portion of tree was removed with in a few days of incident. | 2020-03-20 14:20 | 2017-03-06
OUTAGE ID NUMBER: 170218E116144 | DISTRICT NAME: Orange County | 703 | 362 | 31050 AVENIDA LOS CERRITOS, SAN JUAN CAPO 92675 | Pine | 2017-02-18 | FL1384 | P27996 P27995 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2016-07-15 | N | 10.0 to 11.9 ft | N | 2013-11-26 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | None | 15.1 - 20 |  |  |  |  | No Record | No Record | N | Large branch from pine tree broke out during high wind and rain conditions and fell on primary conductors bringing down two span of wire. There were no known defects in the tree prior to failure. This outage appears unavoidable. |  | The outage tree and another pine on the property were completely removed by the customer's contractor soon after the incident. No other trees on the property currently pose a hazard to the powerlines. No further action required by SDG&E at this time. | 2020-03-20 14:20 | 2017-02-24
OUTAGE ID NUMBER: 170221E116232 | DISTRICT NAME: | 552 | 340 | 3242 ORCHARD HILL RD, BONITA 91902 | Eucalyptus | 2017-02-22 | JK86 | P187339 P187339 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 100.1 ft + | 24.0 to 35.9 in |  | 100.1 - '+' |  |  |  |  | No Record | No Record | N | A very large non-inventory eucalyptus estimated to be 24-36"dbh x 100ft+ tall fell onto nearby Tel-Co wires. The resulting ripple effect caused pole P187339 to fail. Tel-Co impact was two spans away from SDG&E facilities. | N/A | Whole tree failure requires no further work. | 2020-03-20 14:20 | 2017-03-07
OUTAGE ID NUMBER: 170227E116690 | DISTRICT NAME: | 514 | 364 | 3550 EUCLID AVE, SAN DIEGO 92105 | Eucalyptus | 2017-02-27 | JK87 | P838292 P838292 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 60.1 to 80.0 ft | 24.0 to 35.9 in |  | 80.1 - 100 |  |  |  |  | No Record | No Record | N | A large multi trunk non-inventory Eucalyptus fell onto nearby Tel-Co wires in a steep "pocket canyon". The impact to Tel-Co wires attached to P838292 pulled this primary pole to side causing conductors to contact nearby trees and causing the outage on Cir364. Saturated soils and erosion from recent multiple storms played a part in tree failure as well as playing a part for pulling up side down anchors on P838292. | N/A | Tree contractor was called out to safely clear tree from Tel-Co lines. | 2020-03-20 14:20 | 2017-03-07
OUTAGE ID NUMBER: 170227E116715 | DISTRICT NAME: | 403 | LR1 | 3203 KENORA DR, SPRING VALLEY 91977 | Pine | 2017-02-27 | AR2885 | P876476 P876477 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 0.0 to 2.0 ft | Tree Failure | 2017-02-15 | N | 4.1 to 5.9 ft | N | 2016-07-15 | N | 60.1 to 80 ft | 0.0 to 2.0 ft | 18.0 to 23.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A large inventory Alleppo Pine failed at base hit primary and caused 2 poles to fail with wires down. Saturated soils from multiple rain events may have played a role in whole tree failure. | N/A | The tree owner has been a historic "sensative customer" who would not allow tree contractors to "roll the top back" on this tree. Ms Marjoie Barnes allowed minimal compliance trims only and not allow any extensive work in the upper canopy of this particular tree. | 2020-03-20 14:20 | 2017-03-07
OUTAGE ID NUMBER: 170308E117435 | DISTRICT NAME: NC | 304 | 452 | 3139 E VALLEY PKWY, ESCONDIDO 92027 | Avocado | 2017-03-08 | FN5969 | P109761 P109762 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Non-SDGE Crew Caused | 2017-02-07 | Y | 10.0 to 11.9 ft | N | 2016-05-03 | Y | 30.1 to 40 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in | Other | 8.1 - 10 |  |  |  |  | No Record | No Record | N | Private tree contractor working in avocado grove stumping trees. Crew dropped large branch that struck the bell cable shaking the poles that caused the the wires to slap together and blow a fuse. | Spoke to Lupe the grove manager and asked if he was on site when it happened, and if it was his workers. He said it was a private company that did the work and he wasn't there when it happened. Tree contractor was Queretaro tree service, owner Miguel Rodriguez, phone #760 650-6994 | I spoke to the owner and explained the hazards and the laws resrticting private companies from working near energized conductors. I also told him to call SDGE anytime they have work near wires so that we can assist in trimming around the wires. | 2020-03-20 14:20 | 2017-03-09
OUTAGE ID NUMBER: 170402E119396 | DISTRICT NAME: | 510 | 137 | 3575 7TH AVE, SAN DIEGO 92103 | Oak | 2017-04-02 | BB336 | P736233 P736234 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Distribution with Secondary Underbuild | 2.1 to 4.0 ft | Tree Failure | 2016-10-19 | N | 10.0 to 11.9 ft | N | 2017-01-10 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 42.0 to 47.9 in | None | 15.1 - 20 |  |  | Mechanical |  | No Record | No Record | N | Large live-oak failed at root plate and toppled into the service and secondary wires. Primary outage forced to replace pole and clear debris. No sign of root rot or trunk decay. Failure was a function of mechanical root breakage, steep slope, and recent saturated soil. Tree is located in an urban canyon and there was winds in the area at the time. This could also have been a contributing factor. |  | No further work required. Tree is on the ground and will be cut up and removed from site by customer. | 2020-03-20 14:20 | 2017-04-05
OUTAGE ID NUMBER: 170413E120090 | DISTRICT NAME: | 380 | 1234 | 2045 OLD HIGHWAY 395, FALLBROOK 92028 | Sycamore | 2017-04-13 | AW3465 | P510898 P512845 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2017-04-11 | N | 10.0 to 11.9 ft | N | 2016-06-24 | Y | 50.1 to 60 ft | Unable to Verify | 36.0 to 41.9 in | None | 20.1 - 30 | No Record |  | Decayed Branch |  | Weak Branch Attachment | Previous Branch Crack | N | A large inventory Sycamore (AW3465) failed almost halfway up the trunk, splitting along the backside at an old branch union that appeared to be the former tree top that was removed or failed some years before. This prior prune / failure of the tree top caused heart rot from the canopy and into the trunk as evident by past concrete work performed to the base of the tree to cover up a hole created by the heart rot. The weather conditions were clear so it was not a factor; the tree appeared to just finally fail after losing its structural integrity for so long. It was observed that the tree likely twisted and hit the conductors on the way down as it first appeared that the tree fell clear and couldn’t have struck the lines. | An interview with the Pala Mesa Resort Maintenance Supervisor (Al Villicana 760 908-4889 cell) confirmed the tree failed “overnight” and was down when he arrived to work early that morning. He was willing to review and discuss removals at the site to prevent future outages. Several trees were removed from the site after review. | Nothing further required, tree has fallen clear of the conductors. | 2020-03-20 14:20 | 2017-04-17
OUTAGE ID NUMBER: 170418E120453s | DISTRICT NAME: | 518 | 41 |  | Bottlebrush | 2017-04-08 | JK104 | P831813 P831846 | 704 - Line fault/tree trimming | 318 - Tree contact as a result of growth/encroachment |  | Primary |  | Non-SDGE Crew Caused |  | N |  | N |  | N | 5.1 to 15.0 ft | 60.1 to 80.0 ft | 8.0 to 12.9 in | Other | 60.1 - 80 |  |  |  |  | No Record | No Record | N | A National City tree crew responding to a property owner service request to mitigate a small Bottle Brush tree with cracked trunk on a city street tree across street fom primary wires. A small portion of the tree had a SDG&E service wire running through tree. Crews made a cut on tree, it reportedly spun around and pulled service wire, causing shaking and pulling on secondary wires, causing primary wires to slap across street from where tree was located. Alley arm construction may have played a part in amplifying shaking of faclities | National City tree crew Supervisor Miguel Diaz confirms his crews made a cut on this tree and it spun around and pulled service wires. | National City tree crews know, and have called SDG&E to assist clearing trees from high voltage for safety. This seems to be a rare event requiring no further follow up other than Area Forester pointing out the hazards of working around energized conductors. | 2020-03-20 14:20 | 2017-06-13
OUTAGE ID NUMBER: 170423E120822s | DISTRICT NAME: Eastern | 454 | 1166 | 20624 JAPATUL RD, ALPINE 91901 | Oak | 2017-04-23 | SF2938 | P474968 P474967 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2017-01-03 | N | 10.0 to 11.9 ft | N | 2017-03-17 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 60.0 to 80.0 in |  | 30.1 - 40 |  |  | Root Rot |  | No Record | No Record | N | A large inventory Oak (SF2938) failed at base, laid on primary wires for some amount of time before SDG&E contacted and responded. Initial call to emergency services reports "tree is smoking". CAL Fire and SDG&E responded and found tree in contact with primary wires. The line was de-energized for safety. UTS was called out to clear failed tree from conductors. Heavy stream erosion at base of tree from recent heavy rains exposed the holding roots of tree and made the soil in the area very soft. In addition, recent removals of a line of Eucs on this proeprty near this Oak may have expopsed this tree to unfamiliar winds. | Property owner Lorrettta Sconce (619-445-9393) heard "popping sounds" and smelled smoke. She called 911 to report tree fire. | UTS was called out and cleared failed tree from conductors and to assist in restoration. Tree is now on the ground. No further work required here. | 2020-03-20 14:20 | 2017-06-13
OUTAGE ID NUMBER: 170506E121817s | DISTRICT NAME: Eastern | 467 | 79 | 35847 N PEAK WY, JULIAN 92036 | Oak | 2017-05-06 | JK102 | P876350 P872911 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 30.1 to 40 ft | 20.0 to 30.0 ft | 18.0 to 23.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | Y | A dead Oak ( JK102 non-inventory) possibly burned by '07 Cedar Fire fell onto pole P876350 causing facilities to shake resulting in primary outage. Tree was not tall enough to directly hit primary, but did directly hit pole causing the outage (possible line slap). | N/A | Area Forester observed a few other dead trees that have fallen and are hung up on Tel-Co wires in and around this area odd North Peak. A memo to clear all dead trees off SDG&E facilities as well as clearing the subject pole P876350 of fallen Oak debris will be issued. | 2020-03-20 14:20 | 2017-05-17
OUTAGE ID NUMBER: 170507E121834 | DISTRICT NAME: | 370 | 214 | 33613 BAILEY MEADOW RD, PALOMAR MTN 92060 | Oak | 2017-05-07 | AO3960 | P219242 P219243 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 40.1 to 50 ft | Unable to Verify | 8.0 to 12.9 in | None | 15.1 - 20 | No Record |  | Co-dominant Branch |  | Included Bark | No Record | Y | A medium sized limb from a non-inventory Oak (AO3960) failed at the branch union due to snow and wind loads. The branch union was a codominant with included bark but weather was the primary factor as evident by another large limb breakout in an adjacent Oak (AO3961). I paid another visit to the site with the QA Lead Greg Bell and we determined together which tree it was. | No one was home. | Tree was topped to below wires as well as 4 other trees in the area that needed work. | 2020-03-20 14:20 | 2017-05-11
OUTAGE ID NUMBER: 170524E123058 | DISTRICT NAME: | 383 | 231 | 230 BURMA, FALLBROOK 92028 | Eucalyptus | 2017-05-24 | RY1371 | P812972 P166105 | 626 - SDG&E Contractor line fault/tree trimming | 626 - SDG&E Contractor line fault/tree trimming | Private | Primary | 12.0 to 14.9 ft | SDGE Crew Caused | 2017-03-16 | Y | 10.0 to 11.9 ft | N | 2012-06-06 | N | 30.1 to 40 ft | Unable to Verify | 60.0 to 80.0 in | Contractor | 12.1 - 15 | Davey Tree Surgery |  | None |  | No Record | No Record | N | A Davey crew was topping the tree and had a tip-line within the canopy but the person pulling the line was not able to pull the tree top over by himself. The tree had a lean toward the line and the foreman cut through the holding wood of the cut further complicating the tree topping operation. The tree fell toward the lines and made contact. A fuse blew but the line was not brought down and there were no injuries or fires. | None | Better training for crews on tree topping and felling operations. More crew oversight by GF. | 2020-03-20 14:20 | 2017-05-25
OUTAGE ID NUMBER: 170724E127335s | DISTRICT NAME: Eastern | 456 | 553 | 1177 CRYSTAL LN, EL CAJON 92020 | Pine | 2017-07-24 17:18 | AD641 | P770058 P773513 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-10-24 | N | 10.0 to 11.9 ft | N | 2017-01-25 | Y | 30.1 to 40 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  |  |  | No Record | No Record | N | A large line side limb (6-8"dia x 12-14ft) of inventory Alleppo Pine (AD641) failed in calm conditions, swept toward primary, making contact with powerlines causing this outage. | Resident was unaware that thbis tree limb failed and caused outage. | A follow up tree trim memo was generated and forwarded to tree trim contractor as follow up work to make this tree safe. Tree trim contractor UTS has completed the follow up work. | 2020-03-20 14:20 | 2017-08-15
OUTAGE ID NUMBER: 170801E128003s | DISTRICT NAME: | 454 | 355 | 1946 ALPINE CREEK LN, ALPINE 91901 | Eucalyptus | 2017-08-01 13:22 | RN4106 | P373445 P678731 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-12-15 | N | 10.0 to 11.9 ft | N | 2017-03-08 | Y | 50.1 to 60 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 12.1 - 15 |  |  | Mechanical |  | No Record | No Record | N | An inventory Red Iron Bark Eucalyptus (RN4106) had a trunk snap in half in a rain, wind, lightining storm event. The impact was to pole to pole secondary wire. The shaking of the impact to SSC / Triplex caused the primary outage. | Resident was on site the day after repairing the weather head as a result to this tree failure. He pointed out the tree and confirmed this tree caused the outage. | Tree is down and requires no further work. | 2020-03-20 14:20 | 2017-08-15
OUTAGE ID NUMBER: 170801E128010s | DISTRICT NAME: EA | 454 | 357 | 2256 VIA DIEGUENOS, ALPINE 91901 | Sycamore | 2017-08-11 14:23 | EU8585 | P677793 P130336 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2016-12-06 | N | 10.0 to 11.9 ft | N | 2017-08-08 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 18.0 to 23.9 in | None | 15.1 - 20 |  |  | None |  | No Record | No Record | N | A main lead/ stem to an inventory Sycamore (EU8585) growing away (backside ) from conductors was pushed by high winds in a thunderstorm / wind / rain event caused limb to fail onto primary wires causing outage on Cir 357 on 8/1/17. The impact of limb estimated to be 8" x 12-16 ft, caused wires to come down. At this time the National Weather Service had a Thunderstorm warning in the Alpine area. Multiple outages occured in this event. | Resident Nick Casio 619-445-1683 confirms limb struck conductors. AF investigation found many trees in the area had been knocked down in every direction the day after this storm. | Work has been issued to roll back the remaining top of this tree ( EU8585) as well as removing another Sycamore (AE1745) of concern on the property | 2020-03-20 14:20 | 2017-08-11
OUTAGE ID NUMBER: 170801E128012 | DISTRICT NAME: | 384 | 521 | 1191 RIVERVIEW DR, FALLBROOK 92028 | Eucalyptus | 2017-08-01 | CD22 | P18446 P18447 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 30.1 to 40 ft | Unable to Verify | 8.0 to 12.9 in | None | 12.1 - 15 | No Record |  | Co-dominant Branch |  | Included Bark | No Record | N | A poorly tapered, non-inventory lemon Euc had its top break out during a high wind event (high winds were evident in the area as several treetops were broken out and lots of branch and leaf litter lay on the ground as I approached the property). The tree top had an inclusion and codominant and the tree showed evidence that the top failed violently after the wind had forced the brake out (large cracks in standing tree). Indicating a strong wind event caused the defect to fail. The top had fallen on the primary and brought the line down but no fire was reported or observed. | No one was home at the time of the visit but a follow-up removal will be requested of the tree if no permission is granted then the tree will be topped below the primary. | This property could use a removal project also as there are several trees that are problematic and the slope and topography of the property is very conducive to tree failure during high winds and rain. | 2020-03-20 14:20 | 2017-08-03
OUTAGE ID NUMBER: 170806E128343 | DISTRICT NAME: | 703 | 313 | 31412 LA MATANZA ST, SAN JUAN CAPO 92675 | Oak | 2017-08-06 | FG2704 | P23670 P23669 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2016-07-15 | N | 10.0 to 11.9 ft | N | 2016-10-11 | N | 50.1 to 60 ft | Unable to Verify | 60.0 to 80.0 in | None | 20.1 - 30 | No Record |  | Weak Branch Attachment |  | No Record | No Record | N | A large 15in dia limb on an inventory oak (FG2704) failed during a calm sunny day and brought down the lines and broke 2 crossarms. There were no significant wind or weather events. The tree had a defect at a branch union but a major contributing factor was a lot of end weight on the limb. | The property manager was there and was having the branch removed and other branches elevated on the tree to prevent further failures. | Tree fell through lines and is now clear. No other issues at the property. Customer is going to maintain the tree more vigorously. | 2020-03-20 14:20 | 2017-08-07
OUTAGE ID NUMBER: 170808E128473s | DISTRICT NAME: | 210 | 740 | 3014 EVERGREEN ST, SAN DIEGO 92110 | Palm-Date | 2017-08-08 11:43 | SF755 | P2122370375 P2121170362 | 318 - Tree contact as a result of growth/encroachment | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 0.0 to 2.0 ft | Tree Growth | 2016-10-24 | N | 10.0 to 11.9 ft | N | 2017-05-03 | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 36.0 to 41.9 in |  | 0 - 2 |  |  |  |  | No Record | No Record | N | Canary Island Date Palm located on private property (backyard) planted directly under and mid span of primary wires grew into conductors causing arcing and sparking. Adjacent property owner saw smoke and heard "popping noise called 911 to report tree fire. SDFD called SDG&E. SDG&E deenergized for safety. Tree crews responded and cleared the Palm. | Property owners were out of town. I spoke to neighbor who called 911. She confirms this outage was caused by Palm grow in and confirms she called emergency services (911) | Responding tree crews cleared palm with an aggresive trim down to the "heart" This Palm will be monitoired to see if it recovers and if so will be persued for removal off private property. | 2020-03-20 14:20 | 2017-08-15
OUTAGE ID NUMBER: 170828E129905 | DISTRICT NAME: | 651 | 66 | 15740 PUERTA DEL SOL, RANCHO SANTA FE 92067 | Eucalyptus | 2017-08-28 | CE2838 | P312603 P513700 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 50.1 to 60.0 ft | 42.0 to 47.9 in |  | 50.1 - 60 |  |  | Co-dominant Branch |  | Decayed Branch | Weak Branch Attachment | Y | A large non-inventory Euc approx. 90-100ft tall and 55-65ft from the lines, had a large lead break out and fall accross all phases. The lead had included bark at the union with a large amount of decay internally. This caused the branch to fail and resulted in bringing all phasses down. | Resident unavailable | I'm working with home owners and the association on a removal project in that general area | 2020-03-20 14:20 | 2017-09-13
OUTAGE ID NUMBER: 170904E130561 | DISTRICT NAME: | 513 | 1435 | 2827 A ST, SAN DIEGO 92102 | Palm-Feather | 2017-09-04 12:45 | FO2234 | P230972 P2019072861 | 326 - Palm frond contact | 326 - Palm frond contact | Private | Primary | 0.0 to 2.0 ft | Tree Growth | 2016-10-19 | Y | 10.0 to 11.9 ft | N | 2017-05-08 | N | 15.1 to 20.0 ft | 0.0 to 2.0 ft | 8.0 to 12.9 in |  | 6.1 - 8 |  |  |  |  | No Record | No Record | N | Inventory Queen Palm FO2234 frond came in contact (grow in) with lightning arrestor / fuse on riser pole P230972 causing primary outage. Responding ETS cleared frond from primary and restored power. | N/A apartments. | Queen Palm is located on private property (apartments). Multiple offers to remove have been made to apartment managers over the past several years. If latest offer to remove is ignored or declined, then this Palm will be trimmed in such a way as to not interfere with primary wires again (TTK). | 2020-03-20 14:20 | 2017-09-11
OUTAGE ID NUMBER: 170905E130653 | DISTRICT NAME: | 462 | 157 | 1187 BARRETT LAKE RD, DULZURA 91917 | Eucalyptus | 2017-09-05 | JH94 | P175946 P175945 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | Y |  | Y | 80.1 to 200 ft | 60.1 to 80.0 ft | 60.0 to 80.0 in | None | 50.1 - 60 |  |  | Mechanical |  | None | No Record | N | Long vertical leader (~65ft) of a very large (~100ft x 60DBH) non-inventory eucalyptus tree failed along the stem and brought down the primary wire between poles P175945-P175946. There was no rot or structural defect at the specific break site, and it did not fail at the juncture of another leader. The break which occurred approx 30ft above the ground was likely the result of tensional forces applied by the long length and weight of the branch above the break, and by wind.. A small spot fire was ignited in the vegetation by the energized, downed wire resulting in a burn of approx 10ft X 30ft in an area of wild grape, wild rose, and grasses. A resident was the first to respond to the fire and extinguished it before Cal Fire arrived. Veg Mgmt will be performing additional crown reduction on this tree to avoid a repeat incident. | Property ownerJohn Grice was on scene when the outage occurred and was interviewed by Veg Mgmt on 9/7. Customer provided details of the fire and emergency response. | Subject tree will be drastically pruned to reduce crown height. | 2020-03-20 14:20 | 2017-09-07
OUTAGE ID NUMBER: 170906E130779 | DISTRICT NAME: | 651 | 66 | 15187 LAS PLANIDERAS, RANCHO SANTA FE 92067 | Eucalyptus | 2017-09-07 | CE2840 | P419261 P215185 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 80.1 to 200 ft | 60.1 to 80.0 ft | 36.0 to 41.9 in |  | 60.1 - 80 |  |  | Heart Rot |  | No Record | No Record | Y | A large non-inventory Euc approx. 90-100ft tall and 65-75ft north of the conductors, uprroted due to internal heart rot. The lateral bracing roots looked healty but the heart rot decayed the central anchor root and allowed the tree to uproot. The tree fell across both conductors dropping them to the ground. | Spoke to the new owner Mrs. Donnelly. She said the tree was leaning slightly towards the wires and fell over on a calm day. | I am working with the customer on a removal project to thin out some of the tall Eucs that may cause a problem in the future. Work will be done on a project before the end of the month. | 2020-03-20 14:20 | 2017-09-13
OUTAGE ID NUMBER: 170907E130882 | DISTRICT NAME: Northeast | 381 | 233 | 1748 VIA MONSERATE, FALLBROOK 92028 | Eucalyptus | 2017-09-07 | AD3646 | P213051 P213050 | 626 - SDG&E Contractor line fault/tree trimming | 626 - SDG&E Contractor line fault/tree trimming | Private | Primary | 10.0 to 11.9 ft | Non-SDGE Crew Caused | 2017-06-24 | Y | 10.0 to 11.9 ft | N | 2016-08-24 | Y | 20.1 to 30.0 ft | 10.0 to 11.9 ft | 48.0 to 53.9 in | Contractor | 10.1 - 12 | Davey Tree Surgery |  |  |  | No Record | No Record | N | THIS OUTAGE WAS NOT CAUSED IN CONJUNCTION WITH THE ACTIVITY OF PRUNING. Davey tree crew was in the process of entering an electric gate at the entrance to the customer's driveway. The overhead facilities including telco and primary wire are located directly above and cross the driveway. The gear box located on the front of the bucket of the boom truck caught the lowest-positioned telco line as the truck was moving forward, and when the line rebounded off the bucket, the vibration at the pole caused the primary wire above to slap together. This caused the primary wire to arc and fail dropping one wire to the ground. There were no injuries. | Tenant who was present during the incident was a witness. He reported that the climber (second man on crew) was outside the truck to direct the driver into the driveway through the gate. At one point the climber became distracted as he turned to respond to the electronic gate as it started to close. It was at that point that the driver may have thought that he needed to proceed through the gate to prevent it from closing. | Davey performed a safety standdown with all tree crews on the incident. They have also amended their procedure for guiding trucks to include having a second person outside guiding the driver whenever the truck is moving forward and obstacles may be present. | 2020-03-20 14:20 | 2017-09-26
OUTAGE ID NUMBER: 171028E134927 | DISTRICT NAME: | 314 | 521 | 2260 E MISSION RD, FALLBROOK 92028 | Eucalyptus | 2017-10-28 | CD23 | P118955 P118956 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary |  | Non-SDGE Crew Caused |  | Y |  | N |  | Y | 30.1 to 40 ft | Unable to Verify | 24.0 to 35.9 in | Other | 15.1 - 20 | No Record |  |  |  | No Record | No Record | N | A large leader was being removed from a mature non-inventory Euc by a contractor this customer hired. The limb apparently fell toward the line and brought down the primary and broke the crossarms on both poles in the span. No one was injured and no fire was observed or reported. Tree ID CD23 created for outage reporting. | The customer I spoke to, Mrs. Wilkey 949 368-2673, claimed she didn’t see the incident and was in the house. She described that the contractor was performing the work out front when it happed and that his business card was given to the “SDG&E crew” that showed up to make the repairs. She said that her husband would call me back and give me more info and the contractors contact info as well. Mr. never called back and their number continues to hang up on me when I call (no one answers but it disconnects??) and have not been able to catch anyone home during the day. Gates are locked with several aggressive dogs on the property. Access is not possible without owner present. | No work required. Would like to discuss removals at the property but the customer is unresponsive and probably worried about liability. AF will continue to try to contact them but they are resistant to communicating at this time. | 2020-03-20 14:20 | 2017-11-09
OUTAGE ID NUMBER: 171117E136353s | DISTRICT NAME: | 212 | 578 | 1656 MALDEN ST, SAN DIEGO 92109 | Eucalyptus | 2017-11-17 10:58 | RP1121 | P934653 P934655 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2016-12-22 | N | 10.0 to 11.9 ft | N | 2017-03-09 | Y | 50.1 to 60 ft | 8.0 to 9.9 ft | 36.0 to 41.9 in | Other | 15.1 - 20 |  |  |  |  | No Record | No Record | N | A private third party tree trim company was hired by property owner to "lace out" Eucalyptus on private property. Ted Safford Tree Company's climber was in process of cutting limbs when one limb made contact with primary. No injuries were reported. | Af investigating outage in real time noticed private tree company equipment still on site, but no personel on site. Property woner stated they left "for an appointment". AF followed up with a call to tree compamny owner to confirm no injuries and if worker did make contact to seek medical help. Ted Safford (858.272.1566 or 858.692.2294 cell) confirms no injuries. | AF did speak of the dangers of working near energized high voltage wires. Also, offered to assist in any jobs they may have to contact SDG&E Veg Mgmnt to clear / make safe trees with in 10ft of high voltage | 2020-03-20 14:20 | 2018-01-09
OUTAGE ID NUMBER: 171125E136699s | DISTRICT NAME: | 519 | RS1 | 1024 HANOVER ST, SAN DIEGO 92114 | Pepper (California) | 2017-11-25 09:29 | FM2689 | P736679 P170261 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2017-08-07 | Y | 10.0 to 11.9 ft | N | 2015-11-13 | Y | 20.1 to 30.0 ft | 15.0 to 19.9 ft | 13.0 to 17.9 in |  | 15.1 - 20 |  |  | Root Rot |  | No Record | No Record | N | A relatively small, but old inventory Ca Pepper tree (FM2689) failed at base, toppled parallel to primary wires, hit service wire, causing primary wires to slap together casusing a primary outage. | AF notices nothing but a little saw dust at site of time of investigation. All tree components have been removed and cleaned up. AF speaks with first reponding ETS Chris Warren 619.438.1436 and confirms old Ca Pepper toppled into service wires causing primary lines to slap together. | Tree has been removed by property owner. | 2020-03-20 14:20 | 2018-01-09
OUTAGE ID NUMBER: 171207E137535s | DISTRICT NAME: | 514 | 362 | 5038 HAWLEY BLVD, SAN DIEGO 92116 | Palm-Feather | 2018-12-07 09:16 | QW1226 | P734230 P738080 | 428 - Palm tree contact due to storm/wind | 428 - Palm tree contact due to storm/wind | Private | Primary | 10.0 to 11.9 ft | Tree Growth | 2017-11-21 | N | 10.0 to 11.9 ft | N | 2017-02-16 | Y | 30.1 to 40 ft | 6.0 to 7.9 ft | 13.0 to 17.9 in |  | 10.1 - 12 |  |  | None |  | No Record | No Record | N | A 40 ft inventory (QW1226) Queen Palm's frond made contact with primary wires in a strong wind event causing outage on cir 362. | AF spoke to responding ETS Chris Warren 619.438.1436 who confirms he pulled a palm frond off primary wires near given span. AF identified it to be from QW1226. | AF followed up with visit to property owner. Aliana Dall has given SDG&E permission to remove this Queen Palm off private property. | 2020-03-20 14:20 | 2018-01-09
OUTAGE ID NUMBER: 171207E137582 | DISTRICT NAME: | 220 | 492 | 2575 CLAIREMONT DR, SAN DIEGO 92110 | Eucalyptus | 2017-12-07 12:08 | AE2516 | P839613 P839604 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2017-12-04 | Y | 10.0 to 11.9 ft | N | 2017-03-10 | Y | 40.1 to 50 ft | 4.1 to 5.9 ft | 24.0 to 35.9 in | None | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb broke off inventory Eucalyptus AE2516 during a Santa Anna wind event, laid on primary wires causing two outages on two different circuits in the same span. Refer to outage # 171207E137645s on cir 579 as the second outage in the same span. | AF was out in the field and responded to this tree crew request. | The failed limbs were removed for restoration. A follow up removal request was made to onsite apartment manager. Tree is listed for upcoming routine trim cycle. Removal will be pursued. | 2020-03-20 14:20 | 2018-01-09
OUTAGE ID NUMBER: 171207E137643s | DISTRICT NAME: | 406 | 946 | 8855 DALLAS ST, LA MESA 91942 | Eucalyptus | 2017-12-07 09:05 | JK153 | P678512 P678513 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | City | Primary |  | Tree Failure |  | Y |  | N |  | Y | 50.1 to 60 ft | 40.1 to 50.0 ft | 18.0 to 23.9 in | None | 30.1 - 40 |  |  | Co-dominant Branch |  | No Record | No Record | N | A non-inventory eucalyptus (JK153) failed at co-dominate trunknear the soil line, fell down slope and contacted primary wires causing two primary outages. Refer to second outage # 171207E137528s. Same tree caused two circuit outages in same span. The 18" dbh, m-2 x 50ft Euc was located upslope approximately 40 ft off primary wires. | Area Forester was on site with emergency response from LMFD, SDG&E ETS and La Mesa Park Manager. | La Mesa Park Manager Sharon Flack 619.667.1477 has agreed verbally to allow SDG&E to remove any all Eucalyptus on the slope at La Mesisita Park to prevent another outage. AF will seek official city permission (permits) and coordinate this small removal project of 30-40 trees. | 2020-03-20 14:20 | 2018-01-09
OUTAGE ID NUMBER: 171207E37542 | DISTRICT NAME: | 356 | 236 | 829 PINE ST, RAMONA 92065 | Eucalyptus | 2017-12-07 | PX210 | P312345 P312346 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2017-05-16 | N | 15.0 to 19.9 ft | N | 2009-07-21 | Y | 40.1 to 50 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in | None | 20.1 - 30 |  |  | Root Rot |  | No Record | No Record | Y | A large inventory Euc uprooted during high winds and snagged the outside primary distribution line and brought it to the ground. There is a significant amount of decay in the root base that allowed the tree to uproot. The tree had grown into a chain link fence but it didn't appear to be any outward signs of decay such as conchs. Outage was unavoidable. | No resident or troubleman available for comment | None | 2020-03-20 14:20 | 2018-01-10
OUTAGE ID NUMBER: 171210E137763 | DISTRICT NAME: | 392 | 216 | 34404 VALLEY CENTER RD, VALLEY CENTER 92082 | Chinaberry | 2017-12-10 | JH98 | P32239 P32240 | 420 - Tree contact due to storm/high wind | 420 - Tree contact due to storm/high wind | BIA | Other SDGE Facility |  |  |  | N |  | Y |  | Y | 40.1 to 50 ft | 50.1 to 60.0 ft | 24.0 to 35.9 in | None | 50.1 - 60 |  |  |  |  | No Record | No Record | N | During strong wind conditions, a tree branch from a medium-sized, multi-trunk Chinaberry tree (40ft height x 25inch dia) located in the backyard of 34404 Valley Center Rd rubbed the service line running from station pole P32240 to the house. Friction caused fraying of insulation resulting in arcing of the line. Sparks ignited dry vegetation in empty lot behind the house resulting in a fire approximately 120ft x 60ft in size. Fuels in the burned area were mostly light consisting of weeds and a patch of wild watermelon. There were no injuries, and property damage appeared limited to a partially-constructed barbed wire fence located in the vacant lot, and light to heavy charring of approximately 60 vertical fence slats in the backyard of 34404 Valley Center Rd. SDG&E line crew removed a few tree branches and repaired the line. The screenshot below and attached photos taken on December 11 illustrate the scene. The tree in question is not included in the Vegetation Management inventory as it is located next to the service drop only. CPUC General Order 95 does not require minimum clearances for low voltage service lines. A check of Corrective Maintenance Program (CMP) inspection records for pole P32240 dating back to 2001 shows no follow-up orders required for vegetation clearing or the need for tree guard. Vegetation Management will request tree guard installation on service drop as follow-up. Customer indicated they would be trimming the subject tree for additional clearance. | Date/time of incident: December 10, 2017; Approximately 05:30 Location: P32240 located in a vacant lot behind address 34404 Valley Center Rd, Valley Center 92082 (TB 1071-E1). Customer interviewed during investigation: Mary Toscano (760.212.5379) Responding SDG&E Troubleshooter: John McKeown (760.535.2109) Weather conditions at time of incident: | Tree is safe distance from service drop. Customer indicated they would trim the tree further and keep clear of service line. | 2020-03-20 14:20 | 2017-12-11
OUTAGE ID NUMBER: 180108E139439s | DISTRICT NAME: | 520 | 152 | 71 WALNUT DR, CHULA VISTA 91911 | Eucalyptus | 2018-01-09 05:23 | FE3536 | P187074 P86595 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2017-07-12 | N | 10.0 to 11.9 ft | N | 2017-09-14 | Y | 20.1 to 30.0 ft | 8.0 to 9.9 ft | 18.0 to 23.9 in | None | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb detached off inventory Red Iron Bark Eucalyptus (FE3536) in storm, fell onto primary wires between P86595 - P187074, impacting, and pulling prirmary wire down causing the outage. | N/A | Large limb had been cleaned up. Remaining tree appears OK. This inventory tree will be evaluated annually and trimmed as needed in VMS. | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180109E139440s | DISTRICT NAME: | 518 | 1434 | 3485 WEBSTER AVE, SAN DIEGO 92113 | Tamarisk/Salt Cedar | 2018-01-09 05:27 | AQ253 | P735968 P735970 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2017-08-21 | N | 10.0 to 11.9 ft | N | 2017-11-14 | Y | 30.1 to 40 ft | 8.0 to 9.9 ft | 60.0 to 80.0 in |  | 20.1 - 30 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A large limb detached off inventory Tamarisk in storm event laid on primary conductors near P735968 causing outage on Cir 1434. Limb estimated to be 8" x 24ft. was found nearby with contact burn marks on it. | N/A property boarded up 1-19-18. | The offending limb had fallen to ground. Remaining portion of tree appears OK. This inventory tree will be evaluated annually and trimmed when necessary in VMS. | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180109E139449 | DISTRICT NAME: | 306 | 471 | 2999 BERNARDO AVE, ESCONDIDO 92029 | Pine | 2018-02-22 | FI1946 | P211965 P217621 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2017-03-22 | N | 10.0 to 11.9 ft | N | 2014-06-16 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 54.0 to 59.9 in |  | 15.1 - 20 |  |  | Dead Branch |  | No Record | No Record | N | A branch approximately 12-15ft long and 3in diameter broke out of the canopy and cross phased all three phases of the primary and burned down 2 phases. | Spoke to customer and he said ok to roll back crown on next trim | Roll back crown | 2020-03-20 14:20 | 2018-03-13
OUTAGE ID NUMBER: 180109E139467s | DISTRICT NAME: | 212 | ELE1 | 6485 AVENIDA CRESTA, LA JOLLA 92037 | Palm-Fan | 2018-01-09 05:25 | ER5853 | P933273 P734061 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 15.0 to 19.9 ft | Tree Failure | 2018-01-03 | N | 15.0 to 19.9 ft | N | 2017-03-08 | Y | 60.1 to 80 ft | 15.0 to 19.9 ft | 13.0 to 17.9 in |  | 20.1 - 30 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A dead frond detached from inventory Mex Fan Palm (ER5853) in storm, laid on primary wires causing cross phasing on conductors at P731061, leading to damaged lightning arrestor on P2419768493 causing the outage on ELE1. | N/A SD city ROW tree. | The loose fronds had sluffed off this tree. This inventory tree will be evaluated annually and trimmed when necessary in VMS. Tree is currently flagged for upcoming routine tree trim of VMA. | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180109E139471 | DISTRICT NAME: | 212 | 578 | 2500X GARNET AVE, SAN DIEGO 92109 | Eucalyptus | 2018-01-09 09:00 | JK161 | P138021 P138021 | 214 - Line - transformer deenerg./safety | 214 - Line - transformer deenerg./safety | Military |  |  |  |  | N |  | N |  | N | 40.1 to 50 ft | Unable to Verify | 18.0 to 23.9 in | [6 empty] | No Record | No Record | N |  |  |  | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180109E139471s | DISTRICT NAME: | 212 | 578 | 2500X GARNET AVE, SAN DIEGO 92109 | Eucalyptus | 2018-01-09 09:00 | JK161 | P138021 P138021 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Military | Primary |  | Tree Failure |  | N |  | N |  | N | 40.1 to 50 ft | Unable to Verify | 18.0 to 23.9 in | Other |  | No Record |  | Weak Branch Attachment |  | No Record | No Record | N |  |  |  | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180124E140696s | DISTRICT NAME: | 456 | 412 | 1758 DEHESA RD, EL CAJON 92019 | Eucalyptus | 2018-01-24 09:50 | IG33 | P71847 P170725 | 626 - SDG&E Contractor line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 4.1 to 5.9 ft | SDGE Crew Caused | 2017-10-28 | Y | 10.0 to 11.9 ft | N | 2017-01-27 | Y | 15.1 to 20.0 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in | Contractor | 20.1 - 30 | Asplundh Tree Experts |  |  |  | No Record | No Record | N | While trimming assigned work (IG33, etc..) at 1758 Dehesa Rd, SDG&E's qualified tree trim contractor, Utiltiy Tree Service (UTS), made contact with primary wire between (P170725 - P71847) causing primary outage on Cir 412. No injuries or fire. It is believed the lower boom made contact with 12kv primary and Tel-Co span guy. Two burn marks were observed on contractor's tree truck boom. | AF was contacted and responded to location. | This incident has been investigated both internally (SDG&E) and externally (UTS). The findings are being shared with pertinant parties in an effort to prevent a similar incident. The primary wire configuration in the span goes from horizontal on East pole (P71847) to to verticle on West pole (P171725). The three verticle insulators on West pole are set lower on pole. This decreased the safe working space from about 10-12 ft clearance between conductors and grounded Tel-Co on the East side of span to about 6 ft clerance on the West side of same span. It is believed the young / new crew Foreman did not noice or become aware of this suttle change in safe working clearance / space as he was working from East to West in this span and he broke minimum seperation rule causing the outage | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180130E141230s | DISTRICT NAME: | 510 | 90 | 3700X 10TH AVE, SAN DIEGO 92103 | Eucalyptus | 2018-01-30 11:24 | PQ1073 | P131737 P3680 | 626 - SDG&E Contractor line fault/tree trimming | 704 - Line fault/tree trimming | City | Primary | 10.0 to 11.9 ft | Non-SDGE Crew Caused | 2017-10-05 | Y | 12.0 to 14.9 ft | N | 2017-01-13 | Y | 80.1 to 200 ft | 12.0 to 14.9 ft | 24.0 to 35.9 in | Contractor | 20.1 - 30 | Asplundh Tree Experts |  | None |  | No Record | No Record | N | While conducting assigned reliablity tree work on green Eucalyptus (PQ1073) SDG&E's qualified tree trim contractor, Utiltiy Tree Service (UTS), made a couple of roping and rigging judgement and execution errors while cutting and lowering a limb from upper canopy of 80ft tree to the ground. It is believed the limb estimated to be 5" x 25 ft brushed the 12kv primary wire causing the conductor to slip out of old repaired sleeve in the span. This limb contact caused the sleeve to fail and caused primary wire to fall to into tree canopy streching across small "pocket canyon". No injuries or fire. | AF was notified and was on site to investigate. | This incident is being investigated internally (SDG&E) and externally (UTS). The findings will be shared to pertinent groups in an effort to prevent another outage like this. It is believed that improper roping and rigging led to this incident. UTS Foreperson choose to cut too big a limb for small confined drop zone. The tag line was set proper in limb, but did not have a good pulling angle further away from conductors. There was slack in pulling line due to thick understory. The slack led to little or no pulling pressure when needed to pull cut limb away from energized conductors. | 2020-03-20 14:20 | 2018-02-12
OUTAGE ID NUMBER: 180208E142156 | DISTRICT NAME: | 606 | 205 | 2130 FOOTHILL DR, VISTA 92084 | Eucalyptus | 2018-02-08 | FP5254 | P213833 P213834 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 10.0 to 11.9 ft | Non-SDGE Crew Caused | 2018-01-12 | Y | 10.0 to 11.9 ft | Y | 2011-03-24 | Y | 30.1 to 40 ft | Unable to Verify | 13.0 to 17.9 in | Other | 40.1 - 50 | No Record |  | None |  | No Record | No Record | N | A family member, Kyle Medley, of the property owner was removing trees and felled a med sized Euc (FP5254) toward the conductor and brought the lines down and caused a small spot fire (5’X5’). The fire department responded and extinguished the fire. No one was hurt and no one was assisting him. He underestimated the height of the tree as he thought it wasn’t tall enough to strike the lines. No rope was placed in the tree to control the direction of fall and he did not ascend the tree to remove branches or top to a safe height. | The property owner (David Tharp 858 436-6166) was present when the incident happened but was out back and didn’t witness the outage. His nephew (Kyle Medley 760 477-3236) has a contractor’s license but no real experience removing trees. No contract was written between them. | Davey crews will return to the property to reduce the crown of another Euc (FQ1551) the property owner intends to remove. This will prevent any further outages when they perform that work. | 2020-03-20 14:20 | 2018-02-08
OUTAGE ID NUMBER: 180222E143168 | DISTRICT NAME: | 392 | 214 | 17850 S MESA DR, PAUMA VALLEY 92061 | Oak | 2018-02-22 | FP4546 | P215447 P215448 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2017-04-04 | Y | 10.0 to 11.9 ft | Y | 2013-07-19 | N | 40.1 to 50 ft | Unable to Verify | 24.0 to 35.9 in | Other | 6.1 - 8 | No Record |  | Mechanical |  | No Record | No Record | N | A contractor was removing a medium sized Oak, located next to the primary conductor, and cut a large limb that likely rolled out of the canopy and onto the conductor, bringing the wire down. The cuts observed in the tree were all hinge cuts, this, coupled with no rigging rope (witnesses to this contactors previous work on the property stated they didn’t use ropes to lower any branches), didn't allow control of the branches after they were released from the tree. The work appeared to be conducted by a very inexperienced contractor. The fire department responded and extinguished a small fire within the tree adjacent to this property but there were no injuries reported or fires on the ground. | The homeowner (Cherie Snyder 760-212-8030 cell) said she was not there during the event but had hired a contractor to perform the tree work. She was somewhat evasive initially in providing the contact information for the contractor as she had said that she didn't have the number and didn't recall his name. After a lengthy discussion she relented and emailed me the contractor's contact information (Arturo Velazquez 760-468-3784). I called the contractor but have not yet received a return call. | The nursery owner across the street provided some photographs of the fire department response. The tree is clear of the conductor and not a good removal candidate. The customer understands she needs to hire a qualified contractor to finish the work. I pointed out some damage to her fence that looked very recent and was likely caused by this contractor as they appeared to be just cutting branches and letting them fall freely to the ground without any control. No additional work is required here but the customer will call if she decides to remove any trees in the future. | 2020-03-20 14:20 | 2018-02-23
OUTAGE ID NUMBER: 180228E143979 | DISTRICT NAME: Eastern | 455 | 411 | 2070 GRANITE HILLS DR, EL CAJON 92019 | Pine | 2018-02-28 10:46 | AX3223 | P277891 P376673 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Secondary | 4.1 to 5.9 ft | Non-SDGE Crew Caused | 2017-10-23 | N | 10.0 to 11.9 ft | N | 2017-12-27 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 18.0 to 23.9 in |  | 15.1 - 20 |  |  |  |  | No Record | No Record | N | A general contractor working for a realtor hired an unqualified tree trimmer to remove an inventory Pine (AX3223 CP 12/27/17 at 10-12ft). The trimmer climbed into tree and made large cuts. One limb estimated to be 5" x 16-18ft fell toward conductors, hit pole, caused outage, damaged crossarm and transformewr, as well as private property damage below (neighbor's electric gate). The line came down, arced and sparked for some time until responding ETS arrived on scene | AF was able to investigate and speak to general contractor Daniel Prak 619-948-3705. He was working for realtor and hired Miguel Costellanos "Tree Monkey" 619-369-511 to do the tree work on this property. Daniel Prak did not see actual incident, but was on property when incident occured and was very forthcoming and gave good details. Very large 16ft+ limb was cut near conductors. Tree was 10-12 ft away from conductors. Large limb's tag line was set improper at about 25% up on limb. Tag line needed to be further up limb for proper leverage to pull away. Immediatley after incident climber left scene. Not sure / unconfirmed of injuries or not. | Tree is below wires. No further Vegetation follow up required. Eastern district has forwarded all information to claims. | 2020-03-20 14:20 | 2018-03-08
OUTAGE ID NUMBER: 180414E147364 | DISTRICT NAME: | 311 | 920 |  | Eucalyptus | 2018-04-14 | CE2843 | P171877 P171885 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 60.1 to 80.0 ft | 24.0 to 35.9 in |  | 60.1 - 80 |  |  | Decayed Branch |  | No Record | No Record | N | A large branch on a non-inventory Euc broke out due to decay at the base of the branch. The branch struck stub pole P224108s and guy wires connected to pole P171877. This caused the wires between poles P171877-P171878 to shake, cross phase and burn down one leg of primary. |  | The defect would have been clearly visable due to bleeding sap and decay at the base of the branch, but is not in the PI scope of inspections. | 2020-03-20 14:20 | 2018-04-19
OUTAGE ID NUMBER: 180425E148583 | DISTRICT NAME: | 702 | 792 | 34912 CALLE FORTUNA, CAPISTRANO BCH 92624 | Palm-Date | 2018-04-25 | CD24 | P25667 P25668 | 710 - Vehicle contact | 314 - Foreign object in distribution line (balloons | Private | Primary |  | Non-SDGE Crew Caused |  | Y |  | N |  | Y | 30.1 to 40 ft | Unable to Verify | 24.0 to 35.9 in | No Record | 15.1 - 20 | No Record |  | None |  | No Record | No Record | N | A private tree pruning contractor (identified as West Coast Arborists) was pruning a non-inventory Date Palm (CD25 Non-Inventory) and inadvertently swung the boom into the overhead conductor bringing it down. No injuries or fires (on the ground) were reported or observed. | A neighbor (Barbara Hall 949 412-9589 cell) at 34912 Calle Fortuna witnessed the crew hit the lines with the boom and sent me a picture of the truck door, which said “West Coast Arborists”. | No additional work required here but tree(s) are being pursued for removal. | 2020-03-20 14:20 | 2018-04-28
OUTAGE ID NUMBER: 180524E150641s | DISTRICT NAME: Eastern | 450 | 240 | 15216 EL MONTE RD, LAKESIDE 92040 | Silk Oak | 2018-05-24 20:26 | CI2546 | P875102 P875103 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 4.1 to 5.9 ft | Non-SDGE Crew Caused | 2017-11-06 | N | 10.0 to 11.9 ft | N | 2018-03-06 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | No Record | 15.1 - 20 | No Record |  | None |  | No Record | No Record | N | Large inventory California Pepper (CI2546) had been cut with a chainsaw at trunk height , fell toward corner down guy, causing pole P875102 to snap in half and all conductors fall to ground. Responding ETS could find nobody on site responsible for cutting tree. An RDO (equipment vendor) chipper was noted at site and photos snapped of liscence and ETS filled oout damage report. | Area Forester investigates on 5-28-18. Nobody at site to interview. Equipment is gone and wood is stacked. Visible impacts to sorrounding ground shows heavy impact and direction of fall (toward down guy). Large impact, the day (Friday), and time of outage (20:27 = twilight) suggest this tree trimmer was proobably in a hurry to complete the job and get paid before the weekend. | No third party information was obtained by responding ETS or Area Forester on follow up investigation. As of 6-26-18 the 5-23-18 DSOR not published. Information for this report was gathered from responding ETS and Dist Enginer. ON 6-21-18 the 5-24-18 DSOR was published (1 month later) and used for this report. | 2020-03-20 14:20 | 2018-06-26
OUTAGE ID NUMBER: 180524E150641s | DISTRICT NAME: Eastern | 450 | 240 | 15216 EL MONTE RD, LAKESIDE 92040 | Silk Oak | 2018-05-24 20:27 | CI2546 | P875102 P875103 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 4.1 to 5.9 ft | Non-SDGE Crew Caused | 2017-11-06 | N | 10.0 to 11.9 ft | N | 2018-03-06 | Y | 40.1 to 50 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | No Record | 15.1 - 20 | No Record |  | None |  | No Record | No Record | N | Large inventory California Pepper (CI2546) had been cut with a chainsaw at trunk height , fell toward corner down guy, causing pole P875102 to snap in half and all conductors fall to ground. Responding ETS could find nobody on site responsible for cutting tree. An RDO (equipment vendor) chipper was noted at site and photos snapped of liscence and ETS filled oout damage report. | Area Forester investigates on 5-28-18. Nobody at site to interview. Equipment is gone and wood is stacked. Visible impacts to sorrounding ground shows heavy impact and direction of fall (toward down guy). Large impact, the day (Friday), and time of outage (20:27 = twilight) suggest this tree trimmer was proobably in a hurry to complete the job and get paid before the weekend. | No third party information was obtained by responding ETS or Area Forester on follow up investigation. As of 6-26-18 the 5-23-18 DSOR not published. Information for this report was gathered from responding ETS and Dist Enginer. ON 6-21-18 the 5-24-18 DSOR was published (1 month later) and used for this report. | 2020-03-20 14:20 | 2018-06-26
OUTAGE ID NUMBER: 180616E152209s | DISTRICT NAME: | 458 | 356 | 764 S GLEN OAKS DR, ALPINE 91901 | Sycamore | 2018-06-16 23:57 | SQ4233 | P272271 P272272 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 20.0 to 30.0 ft | Tree Failure | 2017-12-22 | N | 10.0 to 11.9 ft | N | 2013-03-05 | Y | 50.1 to 60 ft | 20.0 to 30.0 ft | 24.0 to 35.9 in | None | 50.1 - 60 |  |  |  |  | No Record | No Record | N | A large limb broke off "backside" of inventory syscamore (SQ4233) hit service wire attached to pole P272271 causing probable line slap on primary Cir 356. No injuries, no fire, and no damage to conductors. | Resident James Jewell was home and heard the crash and called SDG&E. I spoke to him on 7/12/18 and he confirms the limb failure of the Sycamore onto service wires. | Large cavity on limb that failed could not be visible from ground inspections. | 2020-03-20 14:20 | 2018-07-30
OUTAGE ID NUMBER: 180624E155572s | DISTRICT NAME: | 477 | 396 | 11410 MANZANITA RD, LAKESIDE 92040 | Pine | 2018-06-24 14:16 | PZ1903 | P474137 P474138 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2018-03-21 | N | 10.0 to 11.9 ft | N | 2018-06-20 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Lower limb detached off inventory Pine (PZ1903), fell onto phone house drop, and pulled secodary wire down in the span causing the primary outage. Tree appeared to have had beetle infestation. | Worker at residence showed AF where the tree was that failed as the inventory Pine. Also pointed out some of the private property damage to house (facia board, and damaged propane tank) confirming the tree as the cause. | Tree was recently trimmed by tree trim contractor (6/20/18) a few days prior to this event (6/24/18). The top of tree was addressed for the primary wires. The limb that failed was lower in tree canopy, over the phone service, away from portion contractor trimmed days prior. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 180803E156020 | DISTRICT NAME: | 652 | 66 | 16224 RAMBLA DE LAS FLORES, RANCHO SANTA FE 92067 | Eucalyptus | 2018-08-03 | JH100 | P15636 P15635 | 704 - Line fault/tree trimming | 622- SDG&E Contractor heavy equip. contact/dig-in | Private |  |  | Non-SDGE Crew Caused |  | N |  | N |  | Y | 20.1 to 30.0 ft | 60.1 to 80.0 ft | 18.0 to 23.9 in | Other | 60.1 - 80 | No Record |  |  |  | No Record | No Record | N | Non-SDG&E tree contractor felled large, non-inventory eucalyptus tree (70' tall; 20" DBH) into primary wire bringing down wire between poles P164938 - P15635. No fire. | Spoke with property owner's mother after incident. Left business card requesting owner to call me back to get information of third-party. Never received back from property owner. | No further action required. Tree was removed by third-party. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 180805E156104s | DISTRICT NAME: Beach Cities | 215 | 64 | 2906 GOBAT AVE, SAN DIEGO 92122 | Palm-Fan | 2018-08-05 16:59 | JA732 | P94300 P94301 | 326 - Palm frond contact | 326 - Palm frond contact | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2018-05-22 | N | 6.0 to 7.9 ft | N | 2017-08-29 | Y | 60.1 to 80 ft | 8.0 to 9.9 ft | 13.0 to 17.9 in | None | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | 8/5/18 DSOR reports of a palm frond found on primary at P94306 caused outage on Cir 64 on 8/5/18. Area Forester invetigates on 12/5/18. There are three inventory Mex Fans one span away that are the likely culprits. This outage will be attributed to closest tallest Mex Fan Palm JA732. | Mrs at residence recalls outage, but declines offer to remove. Trees sit on private property. | Removal offer declined. Trees are in our inventory system and will be maintained trimmed annually. | 2020-03-20 14:20 | 2018-12-06
OUTAGE ID NUMBER: 180814E156900 | DISTRICT NAME: | 310 | Warren Cyn | 13773 PASEO VALLE ALTO, POWAY 92064 | Eucalyptus | 2018-08-14 | FT6723 | Z16516 Z16515 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2018-04-30 | N | 10.0 to 11.9 ft | N | 2016-08-08 | Y | 60.1 to 80 ft | 10.0 to 11.9 ft | 8.0 to 12.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A row of large Eucalyptus trees along the right of way were sloughing bark. A piece of the bark detached from one of the trees and cross phased the distribution line causing the transmission line to fault. I spoke to responding troubleman John Mc Keown and he said he could not confirm the outage report of the 12kv cross phase. He said he pulled several pieces off of single strand primarys but thought the cross phase was on the 69kv conductors. | Resident wants several trees removed | We removed most of the large Eucs that could cause the same problem. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 180917E159342s | DISTRICT NAME: | 456 | 412 | 1755 LISBON LN, EL CAJON 92019 | Eucalyptus | 2018-09-17 19:35 | AD2060 | P475245 P873998 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 20.0 to 30.0 ft | Tree Failure | 2009-10-08 | N | 10.0 to 11.9 ft | N | 2005-12-16 | Y | 50.1 to 60 ft | 40.1 to 50.0 ft | 24.0 to 35.9 in |  | 60.1 - 80 |  |  |  |  | No Record | No Record | N | A very large green non-inventory Eucalyptus (36" dbh x 75-80ft tall) failed at base, fell toward, and impacted primary pole P873998 causing damage to pole and the outage on Cir 412 on 9/17/18. The green tree was beyond our current inventory scope. It failed at base due to subterraining root rot that could not be detected from normal tree inspections. | N/A | Subterraining root rot is very difficult to find on routine visual tree inspections. However, this site did have a large amount (3-4ft) of leaf litter and other vegetation that was very thick around the root clollar. Sometimes this acts like mulch and keeps moisture in the soil around the root zone. This could have induced / enabled the root fungus to be more prevalant. | 2020-03-20 14:20 | 2018-12-06
OUTAGE ID NUMBER: 181112E163325 | DISTRICT NAME: | 393 | 972 | 2458 RAYMOND AVE, RAMONA 92065 | Eucalyptus | 2018-11-12 | QJ4205 | P613807 P718176 | 214 - Line - transformer deenerg./safety | 214 - Line - transformer deenerg./safety | Private | Primary | 15.0 to 19.9 ft | Tree Growth | 2018-03-26 | N | 10.0 to 11.9 ft | N | 2009-05-20 | Y | 30.1 to 40 ft | 15.0 to 19.9 ft | 8.0 to 12.9 in |  | 15.1 - 20 |  |  |  |  | No Record | No Record | N | Lines were de-energized for trimmer and fire safety during the red flag event and high winds. The tree shows no past trim records and sat back at least 15ft from conductors. The tree was very tall (40-50ft) and thin (DBH 13in) which caused severe wind whip during the high winds and caused it to contact the OH wires. The tree was topped to a safe height and won't be a threat for several years. | This is a past refusal and sensative customer. I spoke with Mr Ford for at least an hour and convinced him to remove some of the trees on our next routine cycle. | All potential hazards for any similar event have been trimmed. I will work with customer on future removals. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181112E163382 | DISTRICT NAME: Metro | 520 | 719 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2018-11-12 21:10 | FR6445 | P183981 P729284 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2018-07-24 | N | 10.0 to 11.9 ft | N | 2018-10-16 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 36.0 to 41.9 in |  | 20.1 - 30 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A relatively small limb detached off inventory Euc (FR6445) in a RFW wind event and laid on nearby primary conductors causing the outage. | Tree located on golf ourse and event was after hours. There was no witness. | This tree, and others, on the golf course have been "laid back" away from conductors. An offer to remove all the large Eucalyptus near the powerlines on this golf course was made again. If not accepted, this tree, and others, will be worked as reliabilty prunes. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181113E163393 | DISTRICT NAME: | 623 | 1001 | 3015 LONE JACK RD, ENCINITAS 92024 | Willow | 2018-11-13 | AS1330 | P512595 P325300 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2017-12-18 | N | 10.0 to 11.9 ft | N | 2018-03-15 | Y | 30.1 to 40 ft | 15.0 to 19.9 ft | 8.0 to 12.9 in | None | 15.1 - 20 |  |  |  |  | No Record | No Record | N | Top of willow tree broke out during strong Santa Ana Winds during a RFW event falling onto primary wire. No apparent defect or decay where break occurred. Tree was subsequently topped by Davey below the conductors. |  | Tree will be monitoried and worked during routine operations. Tree is located in riparian area and will be considered for removal. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 181113E163412 | DISTRICT NAME: | 653 | 305 | 17845 VIA DE FORTUNA, RANCHO SANTA FE 92067 | Pine | 2018-11-13 | JH99 | P310122 P512553 | 420 - Tree contact due to storm/high wind | 420 - Tree contact due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 60.1 to 80 ft | 20.0 to 30.0 ft | 24.0 to 35.9 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Codominant branch of a tall (70') pine (20" DBH) broke during strong Santa Ana Winds during a RFW event bringing down one span of primary wire. Break occurred mid-point where the branch was approximately 12" diameter. Break occurred approximately 25' above ground Tree appears otherwise healthy and there was no sign of decay or disease at break point. |  | Tree was trimmed by Davey in response to the outage the same day, and no longer poses a threat to the lines. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 181113E163428 | DISTRICT NAME: | 674 | SF3 | 16837 EL ZORRO VIS, RANCHO SANTA FE 92067 | Eucalyptus | 2018-11-13 | AW4661 | P511030 P512544 | 420 - Tree contact due to storm/high wind | 420 - Tree contact due to storm/high wind | Private | Primary | 0.0 to 2.0 ft | Tree Growth | 2018-11-07 | N | 10.0 to 11.9 ft | N | 2017-11-30 | Y | 20.1 to 30.0 ft | 6.0 to 7.9 ft | 13.0 to 17.9 in | None | 12.1 - 15 |  |  |  |  | No Record | No Record | N | Eucalyptus tree (40' tall; 18" DBH) blew into primary wire during strong Santa Ana winds during RFW event. Davey dispatched day of outage to trim tree. |  | Tree will be pursued for removal with customer during routine operations. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 181113E163428 | DISTRICT NAME: | 673 | 306 | 16417 VIA DE SANTA FE, RANCHO SANTA FE 92067 | Eucalyptus | 2018-11-13 | UG710 | P415378 P415379 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Distribution with Secondary Underbuild | 15.0 to 19.9 ft | Tree Failure | 2017-11-22 | N | 15.0 to 19.9 ft | N | 2014-01-28 | Y | 30.1 to 40 ft | 30.1 to 40.0 ft | 24.0 to 35.9 in | None | 30.1 - 40 |  |  |  |  | No Record | No Record | N | Outage tree indeterminate. Outage occurred during strong Santa Ana Winds during RFW event. Suspect eucalyptus tree located across street from conductors which may have shed a branch during wind landing between primary and secondary wire. No trees underneath or immediately next to lines could have shed the branch. |  | No further action required at this time. Tree will be monitored for future work during routine activity. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 181113E163463 | DISTRICT NAME: | 356 | 236 | 327 PILE ST, RAMONA 92065 | Eucalyptus | 2018-11-13 | SM1926 | P618785 P618786 | 214 - Line - transformer deenerg./safety | 214 - Line - transformer deenerg./safety | Private | Primary | 4.1 to 5.9 ft | Tree Growth | 2018-05-03 | Y | 10.0 to 11.9 ft | N | 2018-08-11 | Y | 20.1 to 30.0 ft | 8.0 to 9.9 ft | 18.0 to 23.9 in |  | 15.1 - 20 |  |  |  |  | No Record | No Record | N | The tree was blowing in high winds on Red Flag event and contacting overhead conductors. The tree had been trimmed in June but had tall whispy branches to the side. Lines were de-energized for tree trimmer and fire safety. Greater clearances should have been obtained during routine trim. |  | Tree was crown reduced and will not be an issue for several years. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181113E163486 | DISTRICT NAME: | 652 | 63 | 16869 REPOSA ALTA, RANCHO SANTA FE 92064 | Eucalyptus | 2018-11-13 | TE39 | P513649 P513650 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2018-10-30 | N | 10.0 to 11.9 ft | N | 2013-12-30 | N | 80.1 to 200 ft | 12.0 to 14.9 ft | 18.0 to 23.9 in | None | 15.1 - 20 |  |  |  |  | No Record | No Record | N | Outage occurred during strong Santa Ana Winds during a RFW event. Specific outage tree indeterminate as there are several eucalyptus trees in the immediate area and there is no longer any visible evidence. Responding ETS reports branch hanging from conductor. |  | Trees in the immediate area appear healthy with good branch attachments. Trees will be monitored and pruned as necessary for growth and reliability during routine activity. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 181113E163499 | DISTRICT NAME: | 365 | 972 | 633 MONTECITO WY, RAMONA 92065 | Eucalyptus | 2018-11-13 | PR10214 | P13284 P13283 | 214 - Line - transformer deenerg./safety | 214 - Line - transformer deenerg./safety | Private | Primary | 10.0 to 11.9 ft | Tree Growth | 2018-04-19 | N |  | N |  | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 13.0 to 17.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | A large Euc approximatley 50-60ft tall was blowing in heavy winds during the red flag event and contacting the primary. The wires were de-energized for tree trimmer and fire safety. | The customer is a past refusal and wouldn't allow removal but the tree was crown reduced below the conductors to make it safe. | No recommendations at this time. I will persue removal during the next routine cycle. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181119E163940 | DISTRICT NAME: | 603 | 1081 | 2101 MANCHESTER AVE, CARDIFF 92007 | Palm-Fan | 2018-11-19 | IT2292 | P25139 P25138 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Growth | 2018-10-19 | N | 10.0 to 11.9 ft | N | 2017-12-09 | Y | 60.1 to 80 ft | 6.0 to 7.9 ft | 13.0 to 17.9 in |  | 6.1 - 8 |  |  |  |  | No Record | No Record | N | The palm is above the lines and 6-8ft to the side. The last trim was 12/17 and several dead fronds had accumulated on the tree. A frond detached and fell accross two phases of the primary knocking a wire loose from the stirup. The wires were de-energized for repair safety. The palms were trimmed afterwards after a request from the troubleman. I spoke to responding troubleman Roland Rodman and he said that he did remember it being windy on the day of the outage. Outage ID; 181119E163821 was also for this same event. | I have not been able to contact the owner but left two voice mails requesting the removal of this palm and one next to it (IT2291). | I will have DRG pursue the removal of these palms. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181123E164074s | DISTRICT NAME: | 462 | 157 | 1187 BARRETT LAKE RD, DULZURA 91917 | Pepper (California) | 2018-11-23 09:01 | EB3758 | P175946 P175945 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2018-08-04 | N | 10.0 to 11.9 ft | N | 2018-10-29 | Y | 30.1 to 40 ft | 10.0 to 11.9 ft | 24.0 to 35.9 in | None | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | Large liomb off inventory Ca Pepper (EB3758) failed and hit primary causing one wire primary wire down. No visible outward sign of decay at point of failure. | Property Owner, Jon Grice (619-468-3041), stated to AF on 1-9-19 that he called SDG&E when he saw the limb hit primary and laid on conductors. "It was not until hours later, that the line came down and SDG&E responded". | An offer to remove this tree was made to Jon Grice. This tree sits on his son's property and he will spaek to son regatrding removal. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181127E164182 | DISTRICT NAME: | 601 | SEA 1 | 461 15TH ST, DEL MAR 92014 | Brush 5X5 Bamboo | 2018-11-27 | SV1225 | P60266 P60267 | 214 - Line - transformer deenerg./safety | 214 - Line - transformer deenerg./safety | Private | Primary | 0.0 to 2.0 ft | Tree Growth | 2018-03-13 | N | 10.0 to 11.9 ft | N | 2018-03-16 | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 0.0 to 2.9 in |  | 0 - 2 |  |  |  |  | No Record | No Record | N | An outage was requested by AF Greg Peck for contractor safety. Bamboo directly below the lines had grown through the conductors and could not be safely trimmed with energized conductors. | The owner refused removal of Bamboo to UTS field supervisor Dennis Sweeney the day of the outage. I also spoke to her and offered stump grind and replacements for removal. I explained the rapid growth and potential danger but she still refused. | Recomend two bamboo patrols yearly to help catch potential shoots before they can reach the conductors | 2020-03-20 14:20 | 2019-01-09
OUTAGE ID NUMBER: 181129E164395 | DISTRICT NAME: North Coast | 351 | 185 | 3023X HILL VALLEY DR, ESCONDIDO 92029 | Avocado | 2018-11-29 | CE2849 | P610171 P610170 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | Y |  | N |  | Y | 50.1 to 60 ft | 30.1 to 40.0 ft | 54.0 to 59.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | Y | A large non-inventory Avocado, 50-60ft tall and 35ft from the lines uprooted and fell accross the lines. The tree showed clear signs of root rot that contributed to it's failure in a rain event. | I spoke to the neighbor that said the line doesn't feed anything. | There are a few other dead Avicados that may present a danger in the future. I will have DRG inspect and flag any hazards. I think these trees should have been identified in the last inspection since they looked to have been dead for at least a few years. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181204E164649 | DISTRICT NAME: | 387 | 354 | 30159 DISNEY LN, VISTA 92084 | Pepper (California) | 2018-12-04 | FM10315 | P612284 P612286 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2018-03-06 | N | 10.0 to 11.9 ft | N | 2018-06-07 | N | 30.1 to 40 ft | Unable to Verify | 60.0 to 80.0 in | None | 10.1 - 12 | No Record |  | Root Rot |  | Girdled Roots | No Record | N | This medium-sized, multi-trunk California Pepper (FM10315) located on a slope and with good branch unions failed at the root plate and brought down the primary conductors on a clear day with no weather activity or winds. The majority of the tree’s weight was located on the line-side as indicated by the size of the leaders on that side of the tree. J-rooting and dead roots were observed on the backside of the root plate located opposite the conductors and uphill which, coupled with the line-side weight, was the primary cause for this outage. The tree appeared healthy otherwise with no heartrot and a vibrant liv-crown ratio. The soil was dry but recent rains were also likely a factor in the tree failing. No fires or injuries were reported or observed. | I spoke to the tenant (Melvin Thomas 619 888-7436 cell) and he didn’t see the incident but gave me the property owner’s number (Viola Fouladi 760 703-0557 cell) to contact about additional tree removals. | The property owner has been contacted as additional trees require removal as they may present the same root issues as the outage tree. No additional work required with this outage tree. | 2020-03-20 14:20 | 2018-12-05
OUTAGE ID NUMBER: 181205E164768 | DISTRICT NAME: | 520 | 719 | 88 L ST, CHULA VISTA 91911 | Eucalyptus | 2018-12-05 20:10 | GW9425 | P186034 P82929 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2018-07-24 | N | 10.0 to 11.9 ft | N | 2017-10-19 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 60.0 to 80.0 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A limb detached off large inventory Eucalyptus (GW9425), laid on conductors in a rain storm causing the outage and damaging the secondary underbuild. | No witness. Tree located on gpolf course and event was after hours. | An offer to remove this and other tall Eucalyptus has been made to this golf course (again). If declined, then this tall euc and others will be pruned for reliabilty. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 18120E165008s | DISTRICT NAME: | 412 | 730 | 1111 LA MESA AVE, SPRING VALLEY 91977 | Eucalyptus | 2018-12-08 12:53 | CI812 | P873329 P873330 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2018-09-25 | N | 10.0 to 11.9 ft | N | 2017-12-21 | Y | 40.1 to 50 ft | 6.0 to 7.9 ft | 13.0 to 17.9 in | Other | 20.1 - 30 |  |  |  |  | No Record | No Record | N | It appears that an inventory Eucalyptus (CI812) was being removed by privete third party or home owner when in the process of removing the tree, the trunk hit the Tel_Co wires, causing the primary wires to slap, most likely the cause of this outage. | Property owner was not available, no phone number listed, and has not responded to door hanger. Responding ETS saw "tree trimmers" in the area. There is evedence of this tree hit / impacted the Tel-Co lines at this location. The event happened on a Saturday (12/08/18) which leads to conclusion of private trimmers or home owner doing the work. | Tree has been completely removed and no longer a threat. | 2020-03-20 14:20 | 2019-01-10
OUTAGE ID NUMBER: 181228E166128 | DISTRICT NAME: | 701 | 200 |  | Brush Very Fast 5x5 | 2018-12-28 | GZ186 | P221469 P221469 | 318 - Tree contact as a result of growth/encroachment | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 2.1 to 4.0 ft | Tree Growth | 2018-08-02 | N | 10.0 to 11.9 ft | N | 2018-09-06 | N | 5.1 to 15.0 ft | Unable to Verify | 0.0 to 2.9 in | None | 0 - 2 | No Record |  | None |  | No Record | No Record | N | A cane from this Giant Bamboo Spp (GZ186) grew into the primary hardware on pole P221469 where the overhead transitions into underground facilities. The clearance is difficult to maintain for this hardware as it brings the energized primary conductors down to around 20ft from the ground. No fire or injuries were reported or observed. The Bamboo was memo pruned 9-1-18 and cane abruption pruning was observed at 4’ and 6’ high as is required in our Bamboo pruning specifications so I am confident the crews did all they could to get down into the clump to abrupt the cane grown at the time of memo prune. | I spoke to the property owner (Mike Meyers 818 219-8879 cell) and they are open to discussing removal of the Bamboo as well as a Date Palm located between the 2 poles at this address. I told him that the Bamboo must be removed. | A follow-up with the customer is scheduled to remove the Bamboo and Palm Spp. | 2020-03-20 14:20 | 2019-01-04
OUTAGE ID NUMBER: 190106E166568s | DISTRICT NAME: | 210 | 52 | 1621 CABLE ST, SAN DIEGO 92107 | Palm-Fan | 2019-01-06 00:05 | FX20214 | P1624 P838937 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | City | Primary | 6.0 to 7.9 ft | Tree Failure | 2018-11-07 | N | 6.0 to 7.9 ft | N | 2018-01-30 | Y | 60.1 to 80 ft | 30.1 to 40.0 ft | 13.0 to 17.9 in |  | 40.1 - 50 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A loose frond detached off an inventory Mexican Fan Plam (FX20214) in stormy conditions, laid on conductors at P1624, causing the outage on Cir 52. | N/A | MFP FX20214 is across street from conductors in SD city ROW. It does not meeet the criteria for SD city removal at this time. It is evaluated annually and trimmed when needed -managed by VMS. | 2020-03-20 14:20 | 2019-08-27
OUTAGE ID NUMBER: 190117E167461 | DISTRICT NAME: | 383 | 233 | 3701 S MISSION RD, FALLBROOK 92028 | Sycamore | 2019-01-17 | AH5228 | P116420 P10202 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2018-03-16 | Y | 10.0 to 11.9 ft | N | 2016-06-09 | N | 20.1 to 30.0 ft | Unable to Verify | 60.0 to 80.0 in | None | 15.1 - 20 | No Record |  | Co-dominant Branch |  | Included Bark | No Record | N | A very large and mature codominant inventory Sycamore (AH5228) with included bark failed at the codom and brought down the primary. The primary had fallen onto a busy road as a result (Mission Rd). The tree was widely spread and the leader that failed was more horizontal than vertical. | Spoke to the property owner (Linda Thorne 760 468-7119 cell) and she said she had called SDG&E 12hrs before the tree failed as she saw it was “splitting”. I found no record of this. | The tree was a GR in 2016 and pruned by Davey 6-9-16 and subsequently failed by QA 8-3-16 and then listed clear by QA 8-26-16. This outage was completely preventable but a poor job of pruning and review of that pruning was allowed to leave this tree out there in the field to fail onto the conductors. A field review of this tree was conducted with Davey, DRG, and WECI management as well SDG&E AF’s to discuss how we can avoid these types of failures within our program from happening again. No additional work required for this tree. | 2020-03-20 14:20 | 2019-01-30
OUTAGE ID NUMBER: 190117E167461 | DISTRICT NAME: | 383 | 233 | 3701 S MISSION RD, FALLBROOK 92028 | Sycamore | 2019-01-17 | AH5228 | P116420 P10202 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2018-03-16 | Y | 10.0 to 11.9 ft | N | 2016-06-09 | N | 20.1 to 30.0 ft | Unable to Verify | 60.0 to 80.0 in | None | 15.1 - 20 | No Record |  | Co-dominant Branch |  | Included Bark | No Record | N | A very large and mature codominant inventory Sycamore (AH5228) with included bark failed at the codom and brought down the primary. The primary had fallen onto a busy road as a result (Mission Rd). The tree was widely spread and the leader that failed was more horizontal than vertical. | Spoke to the property owner (Linda Thorne 760 468-7119 cell) and she said she had called SDG&E 12hrs before the tree failed as she saw it was “splitting”. I found record of this, an ETS was called out but no record of a tree crew call out until the outage occurred (for clean up). | The tree was a GR in 2016 and pruned by Davey 6-9-16 and subsequently failed by QA 8-3-16 and then listed clear by QA 8-26-16. This outage was completely preventable but a poor job of pruning and review of that pruning was allowed to leave this tree out there in the field to fail onto the conductors. A field review of this tree was conducted with Davey, DRG, and WECI management as well SDG&E AF’s to discuss how we can avoid these types of failures within our program from happening again. No additional work required for this tree. | 2020-03-20 14:20 | 2019-01-30
OUTAGE ID NUMBER: 190121E167604s | DISTRICT NAME: | 210 | 51 | 4410 SANTA MONICA AVE, SAN DIEGO 92107 | Pine | 2019-01-21 06:59 | AZ467 | P732334 P839155 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2018-10-24 | N | 10.0 to 11.9 ft | N | 2012-01-11 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 60.0 to 80.0 in |  | 15.1 - 20 |  |  | Mechanical |  | No Record | No Record | N | A very large inventory Torrey Pine tree (AZ467) failed at the base, made direct impact to a residental house, killing two occupants in the house. The large Torrey Pine had a very confined root area that may have been modified by adding a slab for an addition and, or a patio slab / sidewalk where roots may have been compromised during the life of the old tree. The root area was just too small for such a large spreading tree. | N/A | Whole tree failure required no further work. Tree contractor was dispatched to assit private tree company to remove the large tree from under and near SDG&E's facicities. | 2020-03-20 14:20 | 2019-08-27
OUTAGE ID NUMBER: 190131E87322 | DISTRICT NAME: Eastern | 510 | 138 | 2715 DOVE ST, SAN DIEGO 92103 | Eucalyptus | 2016-01-31 19:56 | FM18392 | P231971 P231970 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2015-10-24 | N | 10.0 to 11.9 ft | N | 2016-01-29 | Y | 60.1 to 80 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 20.1 - 30 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A small limb / branch (1" x 4') detatched off inventory Euc FM18392in high winds and rain, fell onto primary wire causing outage on Cir 138. | N/A | No immediate follow up required on this tree. Inventory tree is managed by VMS. | 2020-03-20 14:20 | 2016-04-12
OUTAGE ID NUMBER: 190218E169849s | DISTRICT NAME: | 221 | 439 | 10101 OLD GROVE RD, SAN DIEGO 92131 | Eucalyptus | 2019-02-18 18:19 | JK260 | P90357 P90358 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 60.1 to 80 ft | 20.0 to 30.0 ft | 13.0 to 17.9 in |  | 40.1 - 50 |  |  | Root Rot |  | No Record | No Record | N | A tall non-inventory Euc (12-18" x 60ft) fell toward primary pole due to previous days rainstorm. The whole tree failure made a direct hit on nearby primary pole P930357 causing top of pole to break off, causing the outage on Cir 439. The 60ft tall Eucalyptus tree was located approximately 40ft NE of primary riser pole P90357. | N/A | Tree on ground (whole tree failure) no further work. Other trees in area were evaluated and checked out OK. | 2020-03-20 14:20 | 2019-08-27
OUTAGE ID NUMBER: 190220E170060s | DISTRICT NAME: | 408 | CG2 | 4919 RESMAR RD, LA MESA 91941 | Cypress | 2019-02-20 14:20 | QR447 | P373991 P875335 | 420 - Tree contact due to storm/high wind | 420 - Tree contact due to storm/high wind | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2019-02-04 | N | 6.0 to 7.9 ft | N | 2018-06-27 | Y | 30.1 to 40 ft | 2.1 to 4.0 ft | 18.0 to 23.9 in |  | 8.1 - 10 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb off an inventory Monterey Cypress tree (QR447) got pushed into conductors due to high winds and rain on 2/20/2019. The tree contact caused the outage Cir CG2. | N/A | QR477 is part of our tree inventory system. It has since been trimmed on 6/28/2019 for routine VMA work. It will be evaluated annually and trimmed as needed. | 2020-03-20 14:20 | 2019-08-27
OUTAGE ID NUMBER: 190301E170823s | DISTRICT NAME: | 467 | 79 | 35847 N PEAK WY, JULIAN 92036 | Oak | 2019-03-01 22:15 | EW7012 | P876350 P872911 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2019-01-14 | N | 10.0 to 11.9 ft | N | 2014-07-01 | Y | 20.1 to 30.0 ft | 8.0 to 9.9 ft | 18.0 to 23.9 in |  | 8.1 - 10 |  |  | Weak Branch Attachment |  | No Record | No Record | N | Area Forester is not 100% sure that this outage was caused by tree as reported in 4/09/2019 DSOR. There was very severe weather and snow loads in the area (North Peak) at the time of outage. There is a possibility the pole failed (snapped at Tel-Co level) due to snow loads and severe wheather. Also, another outage (190409E173600s on 4/9/19) shows floating wire nearby P876350 (one span away from this suspect tree) that may have produced the burn marks observed by AF investigation on 4/12/19. There is an inventory Oak (EW7012) tree at referenced pole P872911 for this 4/09/2019 outage that displayed contact burn marks on several limbs. The tree does not appear to be large enough to have broken a pole as reported, but is located right next to the pole (P872911) referenced in the 4/09/2019 DSOR as the cause. It is possible the tree limbs, loaded with snow and ice, was pushed onto conductors by high winds, causing the burn marks on tree, and causing the pole (P872911) to snap as reported. | N/A | To be 100% certain that this relatively small tree caused a pole to snap, more analysis is needed for weather, wind, snow and ice loads at the time of outage. More analysis of the second outage (190409E173600s on 4/9/2019) with reported floatng wire that occured between 3/01/2019 (outage date) and 4/12/2019(AF outage invetigation in the field) to see if that caused the burn marks observed in tree. | 2020-03-20 14:20 | 2019-08-27
OUTAGE ID NUMBER: 190309E174655s | DISTRICT NAME: | 220 | 36 | 7650 MISSION VALLEY RD, SAN DIEGO 92108 | Cottonwood | 2019-03-09 09:25 | JK259 | Z479278 Z479277 | 704 - Line fault/tree trimming | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | SDGE Underground |  | Non-SDGE Crew Caused |  | N |  | N |  | Y | 40.1 to 50 ft | No Record | 13.0 to 17.9 in | Other | 30.1 - 40 |  |  |  |  | No Record | No Record | N | Commercial property owned by Fenton Materials hired Four Seasons Tree trim contractor to remove deseased non-inventory cottonwoods from in front of commercial office TR Hale Business Center at 7480 Mission Valley Rd SD. In an attempt to pull tree away from three story glass covered office building, the tree fell toward and impacted pad mount ntransformer (D109288) causing an underground primary outage on cir 36. | Spoke to faciclities manager Dawn Baker 619-400-0120 who confirms they hired Four Seasons Tree Co (Jake Ashby 760-822-0619) | Four large deseased Cottonwood trees were completely removed from this property. | 2020-03-20 14:20 | 2019-08-26
OUTAGE ID NUMBER: 190330E172867s | DISTRICT NAME: | 456 | 387 | 2185 BROOKHURST DR, EL CAJON 92019 | Liquidambar | 2019-03-30 | AD2485 | P76844 P77193 | 704 - Line fault/tree trimming | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2018-10-22 | N | 10.0 to 11.9 ft | N | 2019-02-01 | Y | 50.1 to 60 ft | 12.0 to 14.9 ft | 18.0 to 23.9 in | Other | 20.1 - 30 |  |  | None |  | No Record | No Record | N | Property owner at 2185 Brookhurst Dr decided to remove an inventory Liquidamber (AD2485) when a poertion of tree limb brushed the primary wires causing a primary outage on Cir 387 due to possible line slap. | Tracy Taylor 619-938-3108 confirms husband was performing the tree removal. confirms vegetation brushed the 12kv. | Tree has been removed. | 2020-03-20 14:20 | 2019-08-26
OUTAGE ID NUMBER: 190610E178116 | DISTRICT NAME: | 390 | 521 | 2172 RAINBOW GLEN RD, FALLBROOK 92028 | Oak | 2019-06-10 | KO241 | P811972 P811973 | 320 - Deenergized for safety tree trimming | 320 - Deenergized for safety tree trimming | Private | Primary | 8.0 to 9.9 ft | No Record | 2019-05-30 | N |  | N |  | N | 15.1 to 20.0 ft | Unable to Verify | 13.0 to 17.9 in | None | 0 - 2 | No Record |  | None |  | No Record | No Record | N | ETS Chris Martinez (760) 330 - 6849) says he found an inventory Oak Tree (tree ID KO241) in contact with primary distribution conductor. He said lines were 17ft 4in from ground when he found them during his patrol and he had them pulled up to 23.5ft. ETS called Edison and their ETS asked tree crew to prune Euc limbs on their lines nearby as well. Oak and Eucs were “flaming” during wind contact on hot breezy day according to ETS Chris Martinez. | No resident onsite. An onsite review was conducted with myself and DRG management to determine if PI (last inspected by James Tuipala 5/30/19) made a bad call with clearances. There was no evidence the line was ever raised (old, weathered equipment and hot tap clamps still present and no new splices or wire were on facilities) as requested by ETS or in contact with our facilities. The ETS, out of an abundance of caution, pulled the fuse and called for a tree crew. It is believed he did see Eucs in contact with the Edison lines directly adjacent to our facilities and the Davey tree crew confirmed this. So it was not likely our facilities had been in contact. | Oak tree was removed, no additional work required. | 2020-03-20 14:20 | 2019-06-17
OUTAGE ID NUMBER: 190611E178202s | DISTRICT NAME: | 420 | BY3 |  | Oak | 2019-06-11 13:52 | JK258 | P771529 P771530 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment |  | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 20.0 to 30.0 ft | 36.0 to 41.9 in |  | 30.1 - 40 |  |  |  |  | No Record | No Record | N | A large trunk from a non-inventory mature Oak (36" dbh x 40ft) snapped in half at approximately 12-15 ft from ground, hit secondary span across street causing outage on primary one span away. There was a large cavity with bee hive at the point where the trunk broke. | N/A | Large tree trunk failure. Tree no longer a threat to SDG&E facilities. | 2020-03-20 14:20 | 2019-08-26
OUTAGE ID NUMBER: 190616E178562s | DISTRICT NAME: | 452 | 240 | 12650 HIGHWAY 67, LAKESIDE 92040 | Eucalyptus | 2019-06-16 15:18 | FV1714 | P672606 P678675 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 710 - Vehicle contact | Private | Primary | 12.0 to 14.9 ft | Tree Failure | 2018-12-03 | N | 12.0 to 14.9 ft | N | 2019-03-02 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 36.0 to 41.9 in |  | 12.1 - 15 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A large lower lateral "backside" limb (18" x 60ft) detached off an inventory Eucalyptus (FV1714), hit Tel-Co lines running seperatley on a different line span located behing this tree, but attached to SDG&E pole P176759. The resulting limb impact onto Tel-Co snapped P176759 in half causing the outage on Cir240. | N/A | The tree was recently trimmed as a Green Reliabilty (3/2/19). All the work was done on the lineside of this tree, making it safe for the primary lines. VMS is not be resposible for the "backside" of this tree unless something obvious was discovered at tree inspection and or when tree was worked by tree trim contractor. This tree and two more on this property has since been removed (6/26/19). | 2020-03-20 14:20 | 2019-08-27
OUTAGE ID NUMBER: 190711E180261s | DISTRICT NAME: | 420 | 386 | 13445 HIGHWAY 8 BUS, EL CAJON 92021 | Oak | 2019-07-11 01:56 | BA1443 | P471308 P578745 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Tree Failure | 2018-11-29 | N | 10.0 to 11.9 ft | N | 2018-07-23 | N | 30.1 to 40 ft | 8.0 to 9.9 ft | 24.0 to 35.9 in |  | 8.1 - 10 |  |  | Decayed Branch |  | No Record | No Record | N | A large lower lateral limb (12-18' x 30ft) detached off a mature inventory Oak tree (BA1443) in calm conditions, hit Tel-Co lines causing cross arms to break on P578745. Primary was de-energized for safety to make the repair caused by Oak limb on Tel-Co. | N/A | Tree crews were dispatched to assist in restoration. Damaged limb was from lower canopy. The rest of tree checks out OK and is manged by VMS, checked annually and trimmed when needed. | 2020-03-20 14:20 | 2019-08-26
OUTAGE ID NUMBER: 190713E180491s | DISTRICT NAME: | 452 | 240 | 11463 MORENO AVE, LAKESIDE 92040 | Eucalyptus | 2019-07-13 | ON3530 | P572797 P678811 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 8.0 to 9.9 ft | Non-SDGE Crew Caused | 2018-11-17 | Y | 10.0 to 11.9 ft | N | 2019-05-01 | Y | 40.1 to 50 ft | 6.0 to 7.9 ft | 18.0 to 23.9 in | Other | 12.1 - 15 |  |  |  |  | No Record | No Record | N | Contractor had climbed into and was in the process of reducing the crown of a tall eucalyptus tree (~ 50 feet tall x 21 inch diameter) located approximately 17 feet north of primary wire. Contractor had already topped several vertical growing branches before the incident. One cut branch (8 feet long x 2 inch diameter) fell into primary wire and was hung up. Cause of shock unknown but contractor may have grabbed the branch or used a tool to try to retrieve it (all speculative). No fire; no ignition. Property owner states he was not at home when the incident occurred, but contractor was able to call him to report the incident. Contractor subsequently taken to hospital for treatment. |  | Tree was removed on 7/19/19 | 2020-03-20 14:20 | 2019-07-14
OUTAGE ID NUMBER: 190803E182130s | DISTRICT NAME: | 552 | 341 | 3017 EQUITATION LN, BONITA 91902 | Eucalyptus | 2019-08-03 19:48 | JK256 | P88271 P88270 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Secondary |  | Tree Failure |  | N |  | N |  | N | 60.1 to 80 ft | 50.1 to 60.0 ft | 24.0 to 35.9 in | None | 40.1 - 50 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A lower lateral limb (12-18" x 40ft) detached off an non-inventory Eucalyptus, hit secodary pole (P280006) and SSC wire. The Euc was located 40ft to side of P280006. Limb estimated to be 40ft long brushed up against pole causing SSC wire down and primary fuses to blow on Cir341. | N/A | Tree was beyond our inventory specifications and no longer a threat to any SDG&E faciclity. | 2020-03-20 14:20 | 2019-08-26
OUTAGE ID NUMBER: 190806E182225s | DISTRICT NAME: | 514 | 343 | 5741 ADELAIDE AVE, SAN DIEGO 92115 | Pine | 2019-08-06 02:52 | JK257 | P170313 P170314 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | N | 60.1 to 80 ft | 20.0 to 30.0 ft | 36.0 to 41.9 in |  | 50.1 - 60 |  |  | Mechanical |  | No Record | No Record | N | A very large non-inventory Alleppo Pine located in backyard of 5709 Adelaide Ave SD snapped at trunk, hit secondary span across alley betweeen P175147 - P174618, causing a few primary poles to snap and primary wires down in mutiple locations. | AF at site for restoration. Appears tree snapped at trunk in calm conditions most likely from heavy lean toward facilcities. Google Street view confirms a very distinct, heavy lean on this tree taken sometime before failure. | This non inventory tree complete failure is no longer a threat to SDG&E faciclities. | 2020-03-20 14:20 | 2019-08-26
OUTAGE ID NUMBER: 190812E182689 | DISTRICT NAME: | 375 | 214 | 34438 CANFIELD RD, PALOMAR MTN 92060 | Oak | 2019-08-12 | PB1246 | P165858 P165863 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 12.0 to 14.9 ft | Non-SDGE Crew Caused | 2005-08-22 | Y |  | N |  | N | 60.1 to 80 ft | Unable to Verify | 24.0 to 35.9 in | Other | 40.1 - 50 | No Record |  |  |  | No Record | No Record | N | A large dead Oak (Tree ID PB1246) that was improperly cut by the property manager as he was trying to fell the tree (for the sale of firewood) but it fell the wrong way toward the overhead primary lines. There were no injuries or fire. The tree is a past inventory tree that was reliability pruned and deleted from the inventory due to not meeting inventory specs and yet the customer was able to fell it into the power lines. The tree had a GR tag on it but it was unreadable. | I spoke to the person who cut the tree (Art Cruz) and his wife (Margie Butcher 925 413-8771 cell) and let them know to contact us in the future if any tree they are cutting can possibly strike the wire or our equipment. The property owner is Ahmed Khatib (909 450-1325 cell). | No additional work is required for this tree. | 2020-03-20 14:20 | 2019-08-14
OUTAGE ID NUMBER: 190814E182897s | DISTRICT NAME: | 527 | 158 | 570 9TH ST, IMPERIAL BEACH 91932 | Palm-Feather | 2019-08-14 14:02 | OZ436 | P88853 P88354 | 318 - Tree contact as a result of growth/encroachment | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 4.1 to 5.9 ft | Tree Growth | 2019-07-25 | Y | 10.0 to 11.9 ft | N | 2018-08-24 | N | 15.1 to 20.0 ft | 0.0 to 2.0 ft | 3.0 to 7.9 in |  | 8.1 - 10 |  |  |  |  | No Record | No Record | N | ETS reports a Palm frond making contact with primary wires at P88853. Appears that inventory Queen Plam OZ436 has made contact with primary wires at 570 9th St IB. Contact burn marks on conductors and burned fronds were found at location the next day by investigating Area Forester. | N/A | Fronds making contact with primary were cleared at time of outage. The insulator pines were moved further apart by District personal as follow up. Four Queen Palms will be removed from this property as agreed upon by owner on 8/30/19. Removals will be forwarded to tree trim contractor. | 2020-03-20 14:20 | 2019-09-04
OUTAGE ID NUMBER: 190817E183119 | DISTRICT NAME: | 702 | 792 | 34682 CALLE LOS ROBLES, CAPISTRANO BCH 92624 | Ficus | 2019-08-17 | ET927 | P25633 P25632 | 704 - Line fault/tree trimming | 704 - Line fault/tree trimming | Private | Primary | 6.0 to 7.9 ft | Non-SDGE Crew Caused | 2019-07-30 | Y | 10.0 to 11.9 ft | N | 2018-10-30 | N | 30.1 to 40 ft | Unable to Verify | 24.0 to 35.9 in | Other | 8.1 - 10 | No Record |  | Included Bark |  | No Record | No Record | N | A medium sized ficus tree was being pollarded by a private contractor (Independent Landscape 949-370-6610) and likely made contact with the Telco our facilities. No injuries or fires were reported. | Eric Johns at 26881 Calle Maria (949 690-6632 cell) said that a private contractor caused the outage. I attempted to speak to the contractor and they did not return my calls. It is highly likely the outage was caused by this contractor. | No additional work is required at this location but the Forester will continue to pursue removal of this pollarded tree. | 2020-03-20 14:20 | 2019-11-20
OUTAGE ID NUMBER: 19081E182868s | DISTRICT NAME: | 527 | 81 | 734 JACINTO PL, CORONADO 92118 | Brush Very Fast 5x5 | 2019-08-14 12:27 | JK261 | P839313 P193289 | 318 - Tree contact as a result of growth/encroachment | 318 - Tree contact as a result of growth/encroachment | Private | Primary |  | Tree Growth |  | Y |  | N |  | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 0.0 to 2.9 in |  | 0 - 2 |  |  |  |  | No Record | No Record | N | A very fast growing vine climbing on P193289 located in backyard of 728 Jacinto Pl Coronado had grown up into and contacting primary facicties. An outage was taken as a safety precaution. Pole located in backyard and had to be climbed. District personel made tha de-energized for safety call. Vine was cleared with out incident. | Mrs at address had originally called in safety check on 6/27/19. There was some mis-communication and delays beyond VM control on Metros part on scheduling this with required Qualified Linemen to climb and clear vine on pole. | On site Working Foreman made the call to de energize for safety. Vine was cleared on 8/14/19 (with this outage). A tree ID has been placed here so VMS can monitor this vine with it's annual inspections of this VMA. | 2020-03-20 14:20 | 2019-09-04
OUTAGE ID NUMBER: 190904E184378s | DISTRICT NAME: | 512 | 168 | 5464 GILBERT DR, SAN DIEGO 92115 | Acacia | 2019-09-04 14:42 | ET5790 | P170741 P170742 | 320 - Deenergized for safety tree trimming | 318 - Tree contact as a result of growth/encroachment | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2018-11-08 | N | 10.0 to 11.9 ft | N | 2019-03-07 | Y | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 36.0 to 41.9 in |  | 2.1 - 4 |  |  | Root Rot |  | No Record | No Record | N | Inventory Acacia tree (ET5790) was found to be out of compliance by tree trim Audit Contractor and called in to tree trim contractor, UTS, as as same day memo on 09/04/2019. Before climbing tree and while performing a job briefing, UTS Foreman discovered a large crack in the trunk of this multi stem tree. Tree had failed and was being cradled by service and phone drops in a small canyon with no lift access. The weight of the climber would have pushed leaning cradled tree, with cracked trunk, into primary 12kv with in inches of making contact as is. UTS called an "all stop", stood down, and called the Area forester with a request to de energize the 12kv. AF assessed the situation and determioned de energize for safety is necessary. Metro District OH Supervisor was contacted and line crew dispatched. A portion of Cir 168 was de energized for safety to clear hazard tree. Hazard tree was cleared with out incident on 09/04/2019. | N/A | No further follow up required on this tree. | 2020-03-20 14:20 | 2020-01-14
OUTAGE ID NUMBER: 190904E184401s | DISTRICT NAME: | 456 | 93 | 11701 SHADOWGLEN RD, EL CAJON 92020 | Ficus | 2019-09-04 14:37 | JK273 | P773269 P773270 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 20.1 to 30.0 ft | 50.1 to 60.0 ft | 18.0 to 23.9 in |  | 50.1 - 60 |  |  | Root Rot |  | No Record | No Record | Y | A non-inventory Ficus (20-30ft x 18-24"dbh) failed at base, fell down slope approximately 50ft, impacting primary end pole (P773270) down guy system, resulting in wire down / primary outage. The Ficus had evidence of root rot (fruiting bodies of Ganoderma sissile) that lead to the whole tree failure. Unusually high wind gust from the Southwest caused tree to topple down slope approximately 50ft down and approximatly 30ft over to impact SDGE facilities. Contractor tree crews (UTS) were dispatched to location to assist in restoration. | N/A | Whole tree failure, no further work required on this Ficus. Other Ficus on property upslope were checked for similar fruiting body signs and nothing found. | 2020-03-20 14:20 | 2019-11-19
OUTAGE ID NUMBER: 191024E188452s | DISTRICT NAME: | 408 | GM2 | 9419 SIERRA VISTA AVE, LA MESA 91941 | Ash | 2019-10-24 08:31 | JR819 | P174599 P174601 | 704 - Line fault/tree trimming | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary | 8.0 to 9.9 ft | Non-SDGE Crew Caused | 2019-02-01 | N | 10.0 to 11.9 ft | N | 2019-06-28 | Y | 40.1 to 50 ft | 12.0 to 14.9 ft | 13.0 to 17.9 in |  | 6.1 - 8 |  |  |  |  | No Record | No Record | N | Originally reported as "1/S 1/W down from P71501 - P174599 due to fallen branch". AF interviews responding Eastern ETS Jim Lester (619-933-2036). ETS states tree workers were in the area. No name or company given. SDG&E tree contractors were shut down on this area due to Extreme FPI and RFW. It became apparent that private tree trimmer working at 9410 Sierra Vista Ave LM, cut an inventory Ash (JR819) on this property, one span from outage location. Limb made contact with Tel-Co lines causing alley arm construction, both on Tel-Co and primary, to shake resulting in line slap (conductors are a mere 12-18" apart here), causing wire down outage. Heavy impact / abrassion mark was observed at Tel-Co line directly in front of this tree. | N/A. Property Owner never returned call to discuss findings. | Private third party should be more careful and, or call SDG&E Veg Mgmnt. | 2020-03-20 14:20 | 2019-11-12
OUTAGE ID NUMBER: 191102E189432s | DISTRICT NAME: | 518 | HL1 | 3952 TEAK ST, SAN DIEGO 92113 | Palm-Date | 2019-11-02 09:17 | EG43 | P1954173588 P191804 | 320 - Deenergized for safety tree trimming | 318 - Tree contact as a result of growth/encroachment | Private | Secondary | 0.0 to 2.0 ft | No Record | 2019-08-21 | N | 2.1 to 4.0 ft | N | 2018-12-14 | N | 40.1 to 50 ft | 0.0 to 2.0 ft | 18.0 to 23.9 in |  | 2.1 - 4 |  |  |  |  | No Record | No Record | N | Canary Island Date Palm (EG43) died due to heavy South American Palm Weevil infestation. It's fronds and thatch was inter-twined with open wire secondary conductors between P191804 to P1954173588. A planned secondary only outage was scheduled for 11/02/2019. Sometime during the operation a decision was made by field personel that the primary switch feeding the secondary had to be opened. The Plam was cleared from conductors and removed with out incident while span was de-energized. | N/A | This Palm was removed on 11/02/2019. Better to catch these fast dying CI Date Palms that are dying due to South American Palm Weevil infestation. A not was sent to Pre-inspection contractor to keep an eye out and make it a high priority to work these as soon as possible when found. | 2020-03-20 14:20 | 2019-11-12
OUTAGE ID NUMBER: 191120E190958s | DISTRICT NAME: | 520 | 255 | 364 5TH AVE, CHULA VISTA 91910 | Eucalyptus | 2019-11-20 12:29 | PX262 | P85072 P83801 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Primary | 10.0 to 11.9 ft | Tree Failure | 2019-07-01 | Y | 10.0 to 11.9 ft | N | 2018-11-30 | Y | 50.1 to 60 ft | 10.0 to 11.9 ft | 8.0 to 12.9 in |  | 15.1 - 20 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A limb (approximately 4" x 18-20ft) detached off an inventory Eucalyptus (PX262) in a rain and wind storm, impacted the primary wire, causing an outage, and several spans of wire down on Cir 255. No fire or ignition. A branch union had signs of weekness (sap from wound at union) that may not have been visible from ground at most recent inspection of tree on 7/01/2019. | N/A | Tree was inspected on 7/01/2019. Weak attachments were called out and tree was awaiting its annual routine VMA trim scheduled for Sept - Oct 2019. Tree trim contractor UTS is behind schedule and is currently (Jan 2020) working this VMA. District choose to take one span of primary down at this location and replace it with pole to pole guy, lessening the risk of another tree failure here. Several similar Eucalyptus trees at this location will be trimmed as Green Reliability to the new pole to pole guy wires as a preventative measure. | 2020-03-20 14:20 | 2020-01-14
OUTAGE ID NUMBER: 191128E191588s | DISTRICT NAME: | 527 | 159 | 1426 9TH ST, IMPERIAL BEACH 91932 | Palm-Fan | 2019-11-28 22:19 | PQ1430 | P182717 P182718 | 430 - Palm frond due to storm/high wind | 430 - Palm frond due to storm/high wind | Private | Primary | 6.0 to 7.9 ft | Tree Failure | 2019-08-01 | N | 12.0 to 14.9 ft | N | 2018-09-28 | Y | 50.1 to 60 ft | 6.0 to 7.9 ft | 13.0 to 17.9 in |  | 6.1 - 8 |  |  | Dead Branch |  | No Record | No Record | N | A dead frond from inventory Mex Fan Palm (PQ1430) detached in wind and rain, fell onto primary conductors, causing the outage on Cir 159. A dead frond with contact burn marks was found at site confirming contact with 12kv primary conductors. | Resident declined removals. | Tree was identified for prune on 8/19/19. VMA 527 was due to be completed on 11/01/2019. Tree contractor UTS is behind schedule. Three inventory Fan Palms at this property will be expidited for trim to prevent another outage here. | 2020-03-20 14:20 | 2019-12-04
OUTAGE ID NUMBER: 191128E191596s | DISTRICT NAME: | 518 | 130 | 3150 MAIN ST, SAN DIEGO 92113 | Eucalyptus | 2019-11-28 23:54 | EY3620 | P1899373383 P232685 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Military | Primary | 12.0 to 14.9 ft | Tree Failure | 2019-08-19 | N | 10.0 to 11.9 ft | N | 2015-11-30 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 18.0 to 23.9 in |  | 20.1 - 30 |  |  |  |  | No Record | No Record | N | A relatively small limb (1" x 4ft) detached off inventory Lemon Gum Eucalyptus ( EY3620) in rain and wind, fell toward conductors, laid across primary wire causing the outage on Cir 130 | N/A US Naval Base | Tree is clear and compliant, appears to be in OK health with no obvious signs of defects. | 2020-03-20 14:20 | 2019-12-04
OUTAGE ID NUMBER: 191129E191616s | DISTRICT NAME: | 527 | 377 | 20 PINE CT, CORONADO 92118 | Palm-Date | 2019-11-29 16:05 | QV4977 | P832677 P1907971173 | 428 - Palm tree contact due to storm/wind | 428 - Palm tree contact due to storm/wind | Private | Primary | 0.0 to 2.0 ft | Tree Growth | 2019-07-31 | Y | 10.0 to 11.9 ft | N | 2019-08-01 | N | 20.1 to 30.0 ft | 0.0 to 2.0 ft | 24.0 to 35.9 in |  | 2.1 - 4 |  |  |  |  | No Record | No Record | N | New growth spike / frond from inventory Canary Island Date Palm (QV4977) made contact with primary wires in wind and rain, causing an outage on Cir 377. | N/A | This tree was memo trimmed on 8/1/19. A removal card was obtained shortly after and was forwarded to tree trim contractor to remove during the routine work in VMA 527. VMA 527 was due 11/1/19. UTS is currently running behind schedule. Tree was cleared from Dist call out 11/29/19. Tree will be removed with in one week. | 2020-03-20 14:20 | 2019-12-04
OUTAGE ID NUMBER: 191214E192534 | DISTRICT NAME: | 604 | 286 | 1433X PIRAEUS ST, ENCINITAS 92024 | Eucalyptus | 2019-12-14 | CE2869 | P25459 P25460 | 322 - Tree/branch/limb fell on the line or other electrical equipment | 322 - Tree/branch/limb fell on the line or other electrical equipment | Private | Primary |  | Tree Failure |  | N |  | N |  | Y | 50.1 to 60 ft | 50.1 to 60.0 ft | 8.0 to 12.9 in |  | 50.1 - 60 |  |  | Root Rot |  | No Record | No Record | N | A non-inventory Eucalyptus uprooted and laid on one phase of the primary blowing a fuse and causing the outage. The root system for the tree failed due to root decay. Heavy bark and leaf debris with surrounding ice plant kept the ground around the base wet and caused the decay. The tree is on an incline and the recent rains loosened the soil around the tree and allowed the tree to fail towards the wires. | No resident available on site for comment | All trees in this span will be trimmed to a safe height of removed if the customer will allow. | 2020-03-20 14:20 | 2019-12-17
OUTAGE ID NUMBER: 191215E192551s | DISTRICT NAME: Metro | 527 | 159 | 910 BEVERLY AVE, IMPERIAL BEACH 91932 | Palm-Fan | 2019-12-15 12:36 | GA739 | P188027 P188026 | 326 - Palm frond contact | 326 - Palm frond contact | Private | Primary | 4.1 to 5.9 ft | Tree Failure | 2019-08-07 | Y | 10.0 to 11.9 ft | N | 2018-10-04 | Y | 60.1 to 80 ft | 4.1 to 5.9 ft | 13.0 to 17.9 in |  | 6.1 - 8 |  |  | Weak Branch Attachment |  | No Record | No Record | N | A loose frond detached from inventory Mex Fan Palm, GA739, fell onto primary conductors, causing the outage on Cir159. No fire or ignition reported. Tree was identified for routine maintence tree trim on 8/17/2019 with pre-inspection. Routine tree trim was scheduled between Aug - Sept 2019. |  | Tree trim contractor, running behind schedule, trimmed this tree on routine (late) on 12/18/19, 3 days after the reported outage. | 2020-03-20 14:20 | 2020-01-14
OUTAGE ID NUMBER: 191216E192645s | DISTRICT NAME: | 468 | 358 | 30 BROWNS RD, ALPINE 91901 | Cottonwood | 2019-12-16 18:47 | QK840 | P176539 P114323 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 322 - Tree/branch/limb fell on the line or other electrical equipment | BIA | Primary | 10.0 to 11.9 ft | Tree Failure | 2019-04-19 | N | 10.0 to 11.9 ft | N | 2017-06-26 | Y | 60.1 to 80 ft | 12.0 to 14.9 ft | 18.0 to 23.9 in |  | 20.1 - 30 |  |  | Root Rot |  | No Record | No Record | N | Inventory Cottonwood (QK840) failed at base, fell toward primary, causing outage with wire down on Cir 358. No fire or ignition reported. Signs of root decay were evident on exposed root plate (post tree failure). Probably not visible to pre-inspectors (pre tree failure). There was Wind Advisory issued by NWS fro San Diego County at time of outage |  | Whole tree failure (tree on ground) requires no follow up. | 2020-03-20 14:20 | 2020-01-14
OUTAGE ID NUMBER: 191223E193129 | DISTRICT NAME: | 510 | MT1 | 3755 WELLBORN ST, SAN DIEGO 92103 | Pine | 2019-12-23 | AP1581 | P235476 P2116971495 | 426 - Tree/branch/limb fell on the line due to storm/high wind | 426 - Tree/branch/limb fell on the line due to storm/high wind | Private | Distribution with Secondary Underbuild | 6.0 to 7.9 ft | Tree Failure | 2019-10-10 | N | 10.0 to 11.9 ft | N | 2019-03-01 | Y | 50.1 to 60 ft | 6.0 to 7.9 ft | 60.0 to 80.0 in | None | 20.1 - 30 |  |  |  |  | No Record | No Record | N | Tree branch in upper canopy of large, Italian Stone Pine broke during rain/wind condtions falling across primary phases. |  | VM will issue to trim for greater clearance above and adjacent to primary wire. Tree is a significant feature in well-manicured landscape and customer would not want it to be removed. | 2020-03-20 14:20 | 2020-01-03